Introduction and Features

## Model                           	Remarks

KFR-70DW/B1	1PH  230V  50Hz  R22

GST24-22L/A  GST24-22R/A	1PH  220V  60Hz  R22

KF-70DW/NA1   KFR-70DW/NA1	1PH  230V  50Hz  R407C

KFR-70RW/NA1 (Communication)

## Model	Remarks

| KFR-100DW/B1-G | 3PH 380V 50Hz R22 |
| --- | --- |
| GST36-22L/A GST 36-22R/A GST36-38L/A GST36-38R/A | 3PH 220V 60Hz R22 3PH 380V 60Hz R22 |
| KF-100DW/NA1-34005 KFR-100DW/NA1-34005 KFR-100DW/NA1-34005 (Communication) | 3PH 400V 50Hz R407C |

## Model	Remarks

| GST60-22L/A GST 60-22R/A GST42-22R/A GST42-22L/A | 3PH 220V 60Hz R22 |
| --- | --- |
| KFR-120DW/B1-G GST60-38L/A GST60-38R/A GST42-38R/A GST42-38L/A | 3PH 380V 50Hz R22 3PH 380V 60Hz R22 3PH 380V 60Hz R22 |
| KF-120DW/NA1-34005 KFR-120DW/NA1-34005 KFR-120DW/NA1-34005(Communication) | 3PH 400V 50Hz R407C |

| Specifications and Technical Parameters |
| --- |
| Model | GST24-22L/A | GST24-22R/A |
| Function | Cooling | Cooling | Heating |
| Power (Phase-Frequency-Voltage) | 1Ph 60Hz 220V | 1Ph 60Hz 220V |
| Total Capacity | (W) | 7000 | 7000 | 8400 |
| Rated power | (W) | 2800 | 2800 | 2800 |
| Rated current | (A) | 12.8 | 12.8 | 12.5 |
| Air flow volume | (m3/h) | 1140 | 1140 |
| Dehumidify volume | (L/h) | 2.3 | 2.3 |
| C.O.P/EER | (W/W) | 2.5 | 2.5 | 3 |
| Indoor unit | Model | GST24-22L/A(I) | GST24-22R/A(I) |
|  | Fan motor speed (r/min) (H/M/L) | 1480/1380/1300 | 1480/1380/1300 |
|  | Output power of motor(W) | 90 | 90 |
|  | Fan type-piece | Centrifugal Fan-4 | Centrifugal Fan-4 |
|  | Diameter-length (mm) | ф125×134 | ф125×134 |
|  | Evaporator | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф7 | ф7 |
|  | Row-fin distance (mm) | 3-1.6 | 3-1.6 |
|  | Extended area of heat exchange (I×H×L) | 1.042×0.19 | 1.042×0.19 |
|  | Swing motor model | MP35CA | MP35CA |
|  | Power of motor (W) | 4 | 4 |
|  | Fuse (A) | PCB5A Transformer 0.2A | PCB5A Transformer 0.2A |
|  | Operating capacitor (μF) | 4 | 4 |
|  | Sound (pressure level) dB(A) | ≤49 | ≤49 |
|  | Dimension (W/D/H) (mm) | 1300×188×600 | 1300×188×600 |
|  | Dimension of package (W/D/H) (mm) | 1414×248×724 | 1414×248×724 |
|  | Net weight/gross weight (kg) | 32/36 | 32/36 |
| Outdoor Unit | Model | GST24-22L/A(0) | GST24-22RA(0) |
|  | Compressor Power | 2800 | 2800 |
|  | Compressor Type | Rotary Type | Rotary Type |
|  | LRA(A) | 72.5 | 72.5 |
|  | Compressor Overload Protector Type | ZR28K3-PFV-522 | Internal Inherent Protector |
|  | Throttle Method | Capillary | Capillary |
|  | Starting Method | Capacitor | Capacitor |
|  | Range of working temperature(℃) | 18℃≤T≤43℃ | 2℃≤T≤43℃ |
|  | Condenser | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф9.52 | ф9.52 |
|  | Row-fin distance (mm) | 2-1.8 | 2-1.8 |
|  | Extended area of heat exchange (I×H×L)mm | 725×813 | 725×813 |
|  | Fan motor speed (rpm) | 780 | 780 |
|  | Rated Power of Motor (W) | 60 | 60 |
|  | Fan type-piece | Axial Flow Fan-1 | Axial Flow Fan-1 |
|  | Fan Diameter (mm) | ф450 | ф450 |
|  | Defrosting Method | Auto | Auto |
|  | Sound (pressure level) dB(A) | ≤61 | ≤61 |
|  | Dimension (W/D/H) (mm) | 950×412×840 | 950×412×840 |
|  | Dimension of package (W/D/H) (mm) | 1100×450×920 | 1100×450×920 |
|  | Net weight/gross weight (kg) | 75/87 | 75/87 |
|  | Refrigerant/Refrigerant Charge (kg) | R22/2.3 | R22/2.5 |
| Connecting Pipe | Length | 5 | 5 |
|  | Outer Diameter | Liquid Pipe | (mm) | ф9.52(3/8”) | ф9.52(3/8”) |
|  |  | Gas Pipe | (mm) | ф16(5/8”) | ф16(5/8”) |
|  | Max. Distance | Height | (m) | 5 | 5 |
|  |  | Length | (m) | 10 | 10 |

| Model | KF-70DW/NA1 | KFR-70DW/NA1 |
| --- | --- | --- |
| Function | Cooling | Cooling | Heating |
| Power (Phase-Frequency-Voltage) | 1Ph 50Hz 230V | 1Ph 50Hz 230V |
| Total Capacity | (W) | 7000 | 7000 | 8500 |
| Rated power | (W) | 3100 | 3000 | 3050 |
| Rated current | (A) | 15.2 | 14.6 | 15.1 |
| Air flow volume | (m3/h) | 1170 | 1170 |
| Dehumidify volume | (L/h) | 2.3 | 2.3 |
| C.O.P/EER | (W/W) | 2.26 | 2.3 | 2.79 |
| Indoor unit | Model | KF-70D/NA1 | KFR-70DW/NA1 |
|  | Fan motor speed (r/min) (H/M/L) | 1360/1280/1240 | 1360/1280/1240 |
|  | Output power of motor(W) | 100 | 100 |
|  | Fan type-piece | Centrifugal Fan-4 | Centrifugal Fan-4 |
|  | Diameter-length (mm) | ф125×134 | ф125×134 |
|  | Evaporator | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф7 | ф7 |
|  | Row-fin distance (mm) | 3-1.6 | 3-1.6 |
|  | Extended area of heat exchange (I×H×L) | 1.042×0.19 | 1.042×0.19 |
|  | Swing motor model | MP35CA | MP35CA |
|  | Power of motor (W) | 4 | 4 |
|  | Fuse (A) | PCB5A Transformer 0.2A | PCB5A Transformer 0.2A |
|  | Sound (pressure level) dB(A) | ≤48 | ≤47 |
|  | Dimension (W/D/H) (mm) | 1300×188×600 | 1300×188×600 |
|  | Dimension of package (W/D/H) (mm) | 1414×248×724 | 1414×248×724 |
|  | Net weight/gross weight (kg) | 32/36 | 32/36 |
| Outdoor Unit | Model | KFR-70W/dNA1 | KFR-70W/dNA1 |
|  | Input Power | 3000 | 2900 | 2950 |
|  | Running Current | 14.5 | 14.2 | 14.7 |
|  | Compressor Model | C-RN220H5B | C-RN220H5B |
|  | Compressor Type | Rotary Type | Rotary Type |
|  | LRA(A) | 75 | 75 |
|  | Compressor Overload Protector Type | Internal Inherent Protector | Internal Inherent Protector |
|  | Throttle Method | Capillary | Capillary |
|  | Starting Method | Capacitor | Capacitor |
|  | Range of working temperature(℃) | 18℃≤T≤43℃ | -7℃≤T≤43℃ |
|  | Condenser | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф9.52 | ф9.52 |
|  | Row-fin distance (mm) | 2-1.8 | 2-1.8 |
|  | Extended area of heat exchange (I×H×L)mm | 725×813 | 725×813 |
|  | Fan motor speed (rpm) | 60/780 | 60/780 |
|  | Fan type-piece | Axial Flow Fan-1 | Axial Flow Fan-1 |
|  | Fan Diameter (mm) | ф450 | ф450 |
|  | Defrosting Method | Auto | Auto |
|  | Sound (pressure level) dB(A) | ≤58 | ≤58 |
|  | Dimension (W/D/H) (mm) | 950×412×840 | 950×412×840 |
|  | Dimension of package (W/D/H) (mm) | 1100×450×920 | 1100×450×920 |
|  | Net weight/gross weight (kg) | 75/87 | 75/87 |
|  | Refrigerant/Refrigerant Charge (kg) | R407C/2.4 | R407C/2.5 |
| Connecting Pipe | Length | 5 | 5 |
|  | Outer Diameter | Liquid Pipe | (mm) | ф9.52(3/8”) | ф9.52(3/8”) |
|  |  | Gas Pipe | (mm) | ф16(5/8”) | ф16(5/8”) |
|  | Max. Distance | Height | (m) | 5 | 5 |
|  |  | Length | (m) | 10 | 10 |

| Model | KFR-70DW/B1 | KFR-100DW/B1-G |
| --- | --- | --- |
| Function | Cooling | Heating | Cooling | Heating |
| Power (Phase-Frequency-Voltage) | 1Ph 50Hz 230V | 3Ph 50Hz 380V |
| Total Capacity | (W) | 7000 | 8400 | 10000 | 11000 |
| Nominal Power | (W) | 3470 | 2955 | 4000 | 3650 |
| Rated power | (W) |  |  | 4260 | 4160 |
| Rated current | (A) | 18.28 | 15.96 | 7.16 | 6.51 |
| Air flow volume | (m3/h) | 1170 | 2100 |
| Dehumidify volume | (L/h) | 2.3 | 2.6 |
| C.O.P/EER | (W/W) | 2.55 | 2.89 | 2.5 | 3 |
| Indoor unit | Model | KFR-70D/B1 | KFR-100D/B1-G |
|  | Fan motor speed (r/min) (H/M/L) | 1360/1280/1240 | 1140/1070/980 |
|  | Output power of motor(W) | 100 | 150 |
|  | Fan Motor Capacitor |  | 4.5 |
|  | Fan type-piece | Centrifugal Fan-4 | Centrifugal Fan-4 |
|  | Diameter-length (mm) | ф125×134 | ф125×134 |
|  | Evaporator | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф7 | ф7 |
|  | Row-fin distance (mm) | 3-1.6 | 3-1.6 |
|  | Extended area of heat exchange (I×H×L) | 1.042×0.19 | 1.34×0.25 |
|  | Swing motor model | MP35CA | MP35CA |
|  | Power of motor (W) | 4 | 4 |
|  | Fuse (A) | PCB5A Transformer 0.2A | PCB5A Transformer 0.2A |
|  | Sound (pressure level) dB(A) | ≤49 | 49/47/45 |
|  | Dimension (W/D/H) (mm) | 1300×188×600 | 1590×238×695 |
|  | Dimension of package (W/D/H) (mm) | 1414×248×724 | 1770×330×830 |
|  | Net weight/gross weight (kg) | 32/36 | 42/53 |
| Outdoor Unit | Model | KFR-70W/dB1 | KFR-100W/dB1-G |
|  | Compressor Model | ZR34KH-PFJ-522 | C-SB303H8A |
|  | Compressor Type | Rotary Type | Rotary Type |
|  | LRA(A) |  | 42 |
|  | Compressor Overload Protector Type | Internal Inherent Protector | Internal Inherent Protector |
|  | Throttle Method | Capillary | Capillary |
|  | Starting Method | Capacitor | Capacitor |
|  | Range of working temperature(℃) | -2℃≤T≤43℃ | -2℃≤T≤43℃ |
|  | Condenser | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф9.52 | ф9.52 |
|  | Row-fin distance (mm) | 2-1.8 | 2-1.8 |
|  | Extended area of heat exchange (I×H×L)mm | 725×813 | 725×813 |
|  | Fan motor speed (rpm) | 780 | 920 |
|  | Rated Power of Motor (W) | 68 | 92 |
|  | Fan Motor Capacitor (μF) | 3.5 | 3.5 |
|  | Air Flow Volume of Outdoor Unit |  | 4000 |
|  | Fan type-piece | Axial Flow Fan-1 | Axial Flow Fan-1 |
|  | Fan Diameter (mm) | ф450 | ф482 |
|  | Defrosting Method | Auto | Auto |
|  | Sound (pressure level) dB(A) | ≤59 | ≤62 |
|  | Dimension (W/D/H) (mm) | 950×412×840 | 1040×410×840 |
|  | Dimension of package (W/D/H) (mm) | 1100×450×920 | 1100×450×880 |
|  | Net weight/gross weight (kg) | 75/87 | 90/105 |
|  | Refrigerant/Refrigerant Charge (kg) | R22/2.5 | R22/3.1 |
| Connecting Pipe | Length | 5 | 5 |
|  | Outer Diameter | Liquid Pipe | (mm) | ф9.52(3/8”) | Ф12(1/2”) |
|  |  | Gas Pipe | (mm) | ф16(5/8”) | ф19(3/4”) |
|  | Max. Distance | Height | (m) | 5 | 5 |
|  |  | Length | (m) | 10 | 10 |

| Model | GST36-22L/A | GST36-22R/A |
| --- | --- | --- |
| Function | Cooling | Cooling | Heating |
| Power (Phase-Frequency-Voltage) | 3Ph 60Hz 220V | 3Ph 60Hz 220V |
| Total Capacity | (W) | 10000 | 10000 | 11000 |
| Nominal Power | (W) | 4200 | 4000 | 3800 |
| Rated power | (W) | 5050 | 5290 | 4780 |
| Rated current | (A) | 16.9 | 17.2 | 15.2 |
| Air flow volume | (m3/h) | 2100 | 2100 |
| Dehumidify volume | (L/h) | 2.6 | 2.6 |
| C.O.P/EER | (W/W) | 2.38 | 2.44 | 2.89 |
| Indoor unit | Model | GST36-22L/A(I) | GST36-22R/A(I) |
|  | Fan motor speed (r/min) (H/M/L) | 1140/1070/980 | 1140/1070/980 |
|  | Output power of motor(W) | 150 | 150 |
|  | Fan Motor Capacitor | 4 | 4 |
|  | Fan type-piece | Centrifugal Fan-4 | Centrifugal Fan-4 |
|  | Diameter-length (mm) | ф155×175 | ф155×175 |
|  | Evaporator | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф7 | ф7 |
|  | Row-fin distance (mm) | 3-1.6 | 3-1.6 |
|  | Extended area of heat exchange (I×H×L) | 1.34×0.25 | 1.34×0.25 |
|  | Swing motor model | MP35CA | MP35CA |
|  | Power of motor (W) | 4 | 4 |
|  | Fuse (A) | PCB5A Transformer 0.2A | PCB5A Transformer 0.2A |
|  | Sound (pressure level) dB(A) | ≤49/46/43 | ≤49/46/43 |
|  | Dimension (W/D/H) (mm) | 1590×238×695 | 1590×238×695 |
|  | Dimension of package (W/D/H) (mm) | 1770×330×830 | 1770×330×830 |
|  | Net weight/gross weight (kg) | 42/53 | 42/53 |
| Outdoor Unit | Model | GST36-22L/A(0) | GST36-22R/A(0) |
|  | Compressor Model | C-SB263H3A | C-SB263H3A |
|  | Compressor Type | Rotary Type | Rotary Type |
|  | LRA(A) | 103-113 | 103-113 |
|  | Compressor Overload Protector Type | Internal Inherent Protector | Internal Inherent Protector |
|  | Throttle Method | Capillary | Capillary |
|  | Starting Method | Capacitor | Capacitor |
|  | Range of working temperature(℃) | -2℃≤T≤43℃ | -2℃≤T≤43℃ |
|  | Condenser | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф9.52 | ф9.52 |
|  | Row-fin distance (mm) | 2-1.4 | 2-1.4 |
|  | Extended area of heat exchange (I×H×L)mm | 813×930 | 813×930 |
|  | Fan motor speed (rpm) | 920 | 920 |
|  | Rated Power of Motor (W) | 92 | 92 |
|  | Fan Motor Capacitor (μF) | 3.5 | 3.5 |
|  | Fan type-piece | Axial Flow Fan-1 | Axial Flow Fan-1 |
|  | Fan Diameter (mm) | ф497 | ф482 |
|  | Defrosting Method | Auto | Auto |
|  | Sound (pressure level) dB(A) | ≤62 | ≤62 |
|  | Dimension (W/D/H) (mm) | 1040×410×840 | 1040×410×840 |
|  | Dimension of package (W/D/H) (mm) | 1100×450×880 | 1100×450×880 |
|  | Net weight/gross weight (kg) | 90/105 | 90/105 |
|  | Refrigerant/Refrigerant Charge (kg) | R22/3.15 | R22/3.15 |
| Connecting Pipe | Length | 5 | 5 |
|  | Outer Diameter | Liquid Pipe | (mm) | Ф12(1/2”) | Ф12(1/2”) |
|  |  | Gas Pipe | (mm) | ф19(3/4”) | ф19(3/4”) |
|  | Max. Distance | Height | (m) | 5 | 5 |
|  |  | Length | (m) | 10 | 10 |

| Model | GST36-38L/A | GST36-38R/A |
| --- | --- | --- |
| Function | Cooling | Cooling | Heating |
| Power (Phase-Frequency-Voltage) | 3Ph 60Hz 380V | 3Ph 60Hz 380V |
| Total Capacity | (W) | 10000 | 10000 | 11000 |
| Nominal Power | (W) | 4350 | 4350 | 3900 |
| Rated power | (W) | 5600 | 5600 | 5150 |
| Rated current | (A) | 10.7 | 10.8 | 9.3 |
| Air flow volume | (m3/h) | 2100 | 2100 |
| Dehumidify volume | (L/h) | 2.6 | 2.6 |
| C.O.P/EER | (W/W) | 2.3 | 2.3 | 2.82 |
| Indoor unit | Model | GST36-38L/A(I) | GST36-38R/A(I) |
|  | Fan motor speed (r/min) (H/M/L) | 1140/1070/980 | 1140/1070/980 |
|  | Output power of motor(W) | 150 | 150 |
|  | Fan Motor Capacitor | 4 | 4 |
|  | Fan type-piece | Centrifugal Fan-4 | Centrifugal Fan-4 |
|  | Diameter-length (mm) | ф155×175 | ф155×175 |
|  | Evaporator | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф7 | ф7 |
|  | Row-fin distance (mm) | 3-1.6 | 3-1.6 |
|  | Extended area of heat exchange (I×H×L) | 1.34×0.25 | 1.34×0.25 |
|  | Swing motor model | MP35CA | MP35CA |
|  | Power of motor (W) | 4 | 4 |
|  | Fuse (A) | PCB5A Transformer 0.2A | PCB5A Transformer 0.2A |
|  | Sound (pressure level) dB(A) | ≤49/46/43 | ≤49/46/43 |
|  | Dimension (W/D/H) (mm) | 1590×238×695 | 1590×238×695 |
|  | Dimension of package (W/D/H) (mm) | 1770×330×830 | 1770×330×830 |
|  | Net weight/gross weight (kg) | 42/53 | 42/53 |
| Outdoor Unit | Model | GST36-38L/A(0) | GST36-38R/A(0) |
|  | Compressor Model | C-SB263H9A | C-SB263H9A |
|  | Compressor Type | Rotary Type | Rotary Type |
|  | LRA(A) | 50 | 50 |
|  | Compressor Overload Protector Type | Internal Inherent Protector | Internal Inherent Protector |
|  | Throttle Method | Capillary | Capillary |
|  | Starting Method | Capacitor | Capacitor |
|  | Range of working temperature (℃) | -2℃≤T≤43℃ | -2℃≤T≤43℃ |
|  | Condenser | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф9.52 | ф9.52 |
|  | Row-fin distance (mm) | 2-1.4 | 2-1.4 |
|  | Extended area of heat exchange (I×H×L)mm | 813×930 | 813×930 |
|  | Fan motor speed (rpm) | 920 | 920 |
|  | Rated Power of Motor (W) | 92 | 92 |
|  | Fan Motor Capacitor (μF) | 1.5 | 1.5 |
|  | Fan type-piece | Axial Flow Fan-1 | Axial Flow Fan-1 |
|  | Fan Diameter (mm) | ф497 | ф497 |
|  | Defrosting Method | Auto | Auto |
|  | Sound (pressure level) dB(A) | ≤62 | ≤62 |
|  | Dimension (W/D/H) (mm) | 1040×410×840 | 1040×410×840 |
|  | Dimension of package (W/D/H) (mm) | 1100×450×880 | 1100×450×880 |
|  | Net weight/gross weight (kg) | 90/105 | 90/105 |
|  | Refrigerant/Refrigerant Charge (kg) | R22/3.15 | R22/3.15 |
| Connecting Pipe | Length | 5 | 5 |
|  | Outer Diameter | Liquid Pipe | (mm) | Ф12(1/2”) | Ф12(1/2”) |
|  |  | Gas Pipe | (mm) | ф19(3/4”) | ф19(3/4”) |
|  | Max. Distance | Height | (m) | 5 | 5 |
|  |  | Length | (m) | 10 | 10 |

| Model | GST42-38L/A | GST42-38R/A |
| --- | --- | --- |
| Function | Cooling | Cooling | Heating |
| Power (Phase-Frequency-Voltage) | 3Ph 60Hz 380V | 3Ph 60Hz 380V |
| Total Capacity | (W) | 12000 | 12000 | 13500 |
| Rated power | (W) | 5050 | 5050 | 5000 |
| Rated current | (A) | 8.1 | 8.1 | 8 |
| Air flow volume | (m3/h) | 2100 | 2100 |
| Dehumidify volume | (L/h) | 1.5 | 1.5 |
| C.O.P/EER | (W/W) | 2.4 | 2.44 | 2.7 |
| Indoor unit | Model | GST42-38L/A(I) | GST42-38R/A(I) |
|  | Fan motor speed (r/min) (H/M/L) | 1100/1000/900 | 1100/1000/900 |
|  | Output power of motor(W) | 150 | 150 |
|  | Fan type-piece | Centrifugal Fan-4 | Centrifugal Fan-4 |
|  | Diameter-length (mm) | ф155×175 | ф155×175 |
|  | Evaporator | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф7 | ф7 |
|  | Row-fin distance (mm) | 3-1.6 | 3-1.6 |
|  | Extended area of heat exchange (I×H×L) | 1.34×0.28 | 1.34×0.28 |
|  | Swing motor model | MP35CA | MP35CA |
|  | Power of motor (W) | 5 | 5 |
|  | Fuse (A) | PCB5A Transformer 0.2A | PCB5A Transformer 0.2A |
|  | Sound (pressure level) dB(A) | ≤55 | ≤55 |
|  | Dimension (W/D/H) (mm) | 1590×238×695 | 1590×238×695 |
|  | Dimension of package (W/D/H) (mm) | 1770×330×830 | 1770×330×830 |
|  | Net weight/gross weight (kg) | 42 | 42 |
| Outdoor Unit | Model | GST42-38L/A(0) | GST42-22R/A(0) |
|  | Compressor Model | C-SB263H3A | C-SB263H3A |
|  | Compressor Type | Rotary Type | Rotary Type |
|  | LRA(A) | 55 | 55 |
|  | Compressor Overload Protector Type | C-SB303H9A | C-SB303H9A |
|  | Throttle Method | Capillary | Capillary |
|  | Starting Method | Capacitor | Capacitor |
|  | Range of working temperature(℃) | 18℃≤T≤43℃ | -7℃≤T≤43℃ |
|  | Condenser | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф9.52 | ф9.52 |
|  | Row-fin distance (mm) | 2-1.8 | 2-1.8 |
|  | Extended area of heat exchange (I×H×L)mm | 725×1218 | 725×1218 |
|  | Fan motor speed (rpm) | 840 | 840 |
|  | Rated Power of Motor (W) | 68 | 68 |
|  | Fan type-piece | Axial Flow Fan-1 | Axial Flow Fan-1 |
|  | Fan Diameter (mm) | ф450 | ф450 |
|  | Defrosting Method | Auto | Auto |
|  | Sound (pressure level) dB(A) | ≤64 | ≤64 |
|  | Dimension (W/D/H) (mm) | 1250×412×950 | 1250×412×950 |
|  | Dimension of package (W/D/H) (mm) | 1295×450×1110 | 1295×450×1110 |
|  | Net weight/gross weight (kg) | 112/133 | 112/133 |
|  | Refrigerant/Refrigerant Charge (kg) | R22/3.95 | R22/3.6 |
| Connecting Pipe | Length | 5 | 5 |
|  | Outer Diameter | Liquid Pipe | (mm) | Ф12(1/2”) | Ф12(1/2”) |
|  |  | Gas Pipe | (mm) | ф19(3/4”) | ф19(3/4”) |
|  | Max. Distance | Height | (m) | 5 | 5 |
|  |  | Length | (m) | 10 | 10 |

| Model | GST42-22L/A | GST42-22R/A |
| --- | --- | --- |
| Function | Cooling | Cooling | Heating |
| Power (Phase-Frequency-Voltage) | 3Ph 60Hz 220V | 3Ph 60Hz 220V |
| Total Capacity | (W) | 12000 | 12000 | 13500 |
| Rated power | (W) | 5100 | 5100 | 5050 |
| Rated current | (A) | 14.4 | 14.4 | 14.2 |
| Air flow volume | (m3/h) | 2100 | 2100 |
| Dehumidify volume | (L/h) | 1.5 | 1.5 |
| C.O.P/EER | (W/W) | 2.4 | 2.4 | 2.7 |
| Indoor unit | Model | GST42-22L/A(I) | GST42-22R/A(I) |
|  | Fan motor speed (r/min) (H/M/L) | 1100/1000/900 | 1100/1000/900 |
|  | Output power of motor(W) | 150 | 150 |
|  | Fan type-piece | Centrifugal Fan-4 | Centrifugal Fan-4 |
|  | Diameter-length (mm) | ф155×175 | ф155×175 |
|  | Evaporator | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф7 | ф7 |
|  | Row-fin distance (mm) | 3-1.6 | 3-1.6 |
|  | Extended area of heat exchange (I×H×L) | 1.34×0.28 | 1.34×0.28 |
|  | Swing motor model | MP35CA | MP35CA |
|  | Power of motor (W) | 5 | 4 |
|  | Fuse (A) | PCB5A Transformer 0.2A | PCB5A Transformer 0.2A |
|  | Sound (pressure level) dB(A) | ≤55 | ≤55 |
|  | Dimension (W/D/H) (mm) | 1590×238×695 | 1590×238×695 |
|  | Dimension of package (W/D/H) (mm) | 1714×330×830 | 1714×330×830 |
|  | Net weight/gross weight (kg) | 42 | 42 |
| Outdoor Unit | Model | GST42-22L/A(0) | GST42-22R/A(0) |
|  | Compressor Power | 4900 | 4900 |
|  | Compressor Type | Rotary Type | Rotary Type |
|  | LRA(A) | 112 | 112 |
|  | Compressor Overload Protector Type | C-SB303H9A | C-SB303H9A |
|  | Throttle Method | Capillary | Capillary |
|  | Starting Method | Capacitor | Capacitor |
|  | Range of working temperature(℃) | 18℃≤T≤43℃ | -7℃≤T≤43℃ |
|  | Condenser | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф9.52 | ф9.52 |
|  | Row-fin distance (mm) | 2-1.8 | 2-1.8 |
|  | Extended area of heat exchange (I×H×L)mm | 725×1218 | 725×1218 |
|  | Fan motor speed (rpm) | 840 | 840 |
|  | Rated Power of Motor (W) | 68 | 68 |
|  | Fan type-piece | Axial Flow Fan-1 | Axial Flow Fan-1 |
|  | Fan Diameter (mm) | ф450 | ф450 |
|  | Defrosting Method | Auto | Auto |
|  | Sound (pressure level) dB(A) | ≤64 | ≤64 |
|  | Dimension (W/D/H) (mm) | 1250×412×950 | 1250×412×950 |
|  | Dimension of package (W/D/H) (mm) | 1295×450×1110 | 1295×450×1110 |
|  | Net weight/gross weight (kg) | 112/133 | 112/133 |
|  | Refrigerant/Refrigerant Charge (kg) | R22/3.6 | R22/3.6 |
| Connecting Pipe | Length | 5 | 5 |
|  | Outer Diameter | Liquid Pipe | (mm) | Ф12(1/2”) | Ф12(1/2”) |
|  |  | Gas Pipe | (mm) | ф19(3/4”) | ф19(3/4”) |
|  | Max. Distance | Height | (m) | 5 | 5 |
|  |  | Length | (m) | 10 | 10 |

| Model | KF-100DW/NA1-34005 | KFR-100DW/NA1-34005 |
| --- | --- | --- |
| Function | Cooling | Cooling | Heating |
| Power (Phase-Frequency-Voltage) | 3Ph – 400V – 50Hz | 3Ph – 400V – 50Hz |
| Total Capacity | (W) | 10000 | 10000 | 11500 |
| Rated power | (W) | 4250 | 4400 | 4400 |
| Rated current | (A) | 7.4 | 7.5 | 7.6 |
| Air flow volume | (m3/h) | 2100 | 2100 |
| Dehumidify volume | (L/h) | 2.6 | 2.6 |
| C.O.P/EER | (W/W) | 2.35 | 2.27 | 2.61 |
| Indoor unit | Model | KF-100D/NA1-34005 | KFR-100D/NA1-34005 |
|  | Fan motor speed (r/min) (H/M/L) | 1140/1070/980 | 1140/1070/980 |
|  | Output power of motor(W) | 150 | 150 |
|  | Fan type-piece | Centrifugal Fan-4 | Centrifugal Fan-4 |
|  | Diameter-length (mm) | ф155×175 | ф155×175 |
|  | Evaporator | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф7 | ф7 |
|  | Row-fin distance (mm) | 3-1.6 | 3-1.6 |
|  | Extended area of heat exchange (I×H×L) | 1.34×0.25 | 1.34×0.25 |
|  | Swing motor model | MP35CA | MP35CA |
|  | Power of motor (W) | 4 | 4 |
|  | Fuse (A) | PCB5A Transformer 0.2A | PCB5A Transformer 0.2A |
|  | Sound (pressure level) dB(A) | ≤50 | ≤52 |
|  | Dimension (W/D/H) (mm) | 1590×238×695 | 1590×238×695 |
|  | Dimension of package (W/D/H) (mm) | 1770×330×830 | 1770×330×830 |
|  | Net weight/gross weight (kg) | 42/53 | 42/53 |
| Outdoor Unit | Model | KF-100W/dNA1-34005 | KFR-100W/dNA1-34005 |
|  | Compressor Model | C-SB263H3A | C-SB263H3A |
|  | Input Power | 4100 | 4250 | 4250 |
|  | Running Current | 6.8 | 6.9 | 7 |
|  | Compressor Type | Rotary Type | Rotary Type |
|  | LRA(A) | 42 | 42 |
|  | Compressor Overload Protector Type | Internal Inherent Protector | Internal Inherent Protector |
|  | Throttle Method | Capillary | Capillary |
|  | Starting Method | Capacitor | Capacitor |
|  | Range of working temperature(℃) | 18℃≤T≤43℃ | -7℃≤T≤43℃ |
|  | Condenser | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф9.52 | ф9.52 |
|  | Row-fin distance (mm) | 2-1.4 | 2-1.4 |
|  | Working Area mm2 | 813×930 | 813×930 |
|  | Fan motor speed (rpm) | 920 | 920 |
|  | Fan type-piece | Axial Flow Fan-1 | Axial Flow Fan-1 |
|  | Fan Diameter (mm) | ф482 | ф482 |
|  | Defrosting Method | Auto | Auto |
|  | Sound (pressure level) dB(A) | ≤62 | ≤62 |
|  | Dimension (W/D/H) (mm) | 1040×410×840 | 1040×410×840 |
|  | Dimension of package (W/D/H) (mm) | 1100×450×880 | 1100×450×880 |
|  | Net weight/gross weight (kg) | 90/105 | 90/105 |
|  | Refrigerant/Refrigerant Charge (kg) | R407C/3 | R407C/3.1 |
| Connecting Pipe | Length | 5 | 5 |
|  | Outer Diameter | Liquid Pipe | (mm) | Ф12(1/2”) | Ф12(1/2”) |
|  |  | Gas Pipe | (mm) | ф19(3/4”) | ф19(3/4”) |
|  | Max. Distance | Height | (m) | 5 | 5 |
|  |  | Length | (m) | 10 | 10 |

| Model | KF-120DW/NA1-34005 | KFR-120DW/NA1-34005 |
| --- | --- | --- |
| Function | Cooling | Heating | Cooling | Heating |
| Power (Phase-Frequency-Voltage) | 3Ph – 400V – 50Hz | 3Ph – 400V – 50Hz |
| Total Capacity | (W) | 12000 | 12000 | 13000 |
| Rated power | (W) | 5300 | 5000 | 4600 |
| Rated current | (A) | 8.9 | 8.3 | 7.8 |
| Air flow volume | (m3/h) | 2200 | 2200 |
| Dehumidify volume | (L/h) | 3.4 | 3.4 |
| C.O.P/EER | (W/W) | 2.6 | 2.4 | 2.83 |
| Indoor unit | Model | KF-120D/NA1-34005 | KFR-120D/NA1-34005 |
|  | Fan motor speed (r/min) (H/M/L) | 1100/1000/900 | 1100/1000/900 |
|  | Output power of motor(W) | 150 | 150 |
|  | Fan type-piece | Centrifugal Fan-4 | Centrifugal Fan-4 |
|  | Diameter-length (mm) | ф155×175 | ф155×175 |
|  | Evaporator | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф7 | ф7 |
|  | Row-fin distance (mm) | 3-1.6 | 3-1.6 |
|  | Extended area of heat exchange (I×H×L) | 1.34×0.25 | 1.34×0.25 |
|  | Swing motor model | MP35CA | MP35CA |
|  | Power of motor (W) | 4 | 4 |
|  | Fuse (A) | PCB5A Transformer 0.2A | PCB5A Transformer 0.2A |
|  | Sound (pressure level) dB(A) | ≤55 | ≤55 |
|  | Dimension (W/D/H) (mm) | 1590×238×695 | 1590×238×695 |
|  | Dimension of package (W/D/H) (mm) | 1770×330×830 | 1770×330×830 |
|  | Net weight/gross weight (kg) | 42/51 | 42/51 |
| Outdoor Unit | Model | KF-120W/dNA1-34004 | KFR-120W/dNA1-34004 |
|  | Compressor Model | C-SB353H8A | C-SB353H8A |
|  | Input Power | 5150 | 4850 | 4450 |
|  | Running Current | 8.2 | 7.6 | 7.1 |
|  | Compressor Type | Rotary Type | Rotary Type |
|  | LRA(A) | 55 | 55 |
|  | Compressor Overload Protector Type | Internal Inherent Protector | Internal Inherent Protector |
|  | Throttle Method | Capillary | Capillary |
|  | Starting Method | Capacitor | Capacitor |
|  | Range of working temperature(℃) | 18℃≤T≤43℃ | -7℃≤T≤43℃ |
|  | Condenser | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф9.52 | ф9.52 |
|  | Row-fin distance (mm) | 2-1.8 | 2-1.8 |
|  | Working Area mm2 | 725×1218 | 725×1218 |
|  | Fan motor speed (rpm) | 68/840 | 68/840 |
|  | Fan type-piece | Axial Flow Fan-2 | Axial Flow Fan-2 |
|  | Fan Diameter (mm) | ф450 | ф450 |
|  | Defrosting Method | Auto | Auto |
|  | Sound (pressure level) dB(A) | ≤63 | ≤63 |
|  | Dimension (W/D/H) (mm) | 1250×950×412 | 1250×950×412 |
|  | Dimension of package (W/D/H) (mm) | 1295×1110×450 | 1295×1110×450 |
|  | Net weight/gross weight (kg) | 112/133 | 112/133 |
|  | Refrigerant/Refrigerant Charge (kg) | R407C/3.3 | R407C/3.4 |
| Connecting Pipe | Length | 5 | 5 |
|  | Outer Diameter | Liquid Pipe | (mm) | Ф12(1/2”) | Ф12(1/2”) |
|  |  | Gas Pipe | (mm) | ф19(3/4”) | ф19(3/4”) |
|  | Max. Distance | Height | (m) | 5 | 5 |
|  |  | Length | (m) | 10 | 10 |

| Model | GST60-22L/A | GST60-22R/A |
| --- | --- | --- |
| Function | Cooling | Cooling | Heating |
| Power (Phase-Frequency-Voltage) | 3Ph 60Hz 220V | 3Ph 60Hz 220V |
| Total Capacity | (W) | 13000 | 13000 | 14500 |
| Rated power | (W) | 6050 | 6050 | 6200 |
| Rated current | (A) | 17.9 | 17.9 | 18.2 |
| Air flow volume | (m3/h) | 2300 | 2300 |
| Dehumidify volume | (L/h) | 1.5 | 1.5 |
| C.O.P/EER | (W/W) | 2.1 | 2.1 | 2.3 |
| Indoor unit | Model | GST60-22L/A(I) | GST60-22R/A(I) |
|  | Fan motor speed (r/min) (H/M/L) | 1300/1200/1100 | 1300/1200/1100 |
|  | Output power of motor(W) | 180 | 180 |
|  | Fan type-piece | Centrifugal Fan-4 | Centrifugal Fan-4 |
|  | Diameter-length (mm) | ф155×175 | ф155×175 |
|  | Evaporator | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф7 | ф7 |
|  | Row-fin distance (mm) | 3-1.6 | 3-1.6 |
|  | Extended area of heat exchange (I×H×L) | 1.34×0.28 | 1.34×0.28 |
|  | Swing motor model | MP35CA | MP35CA |
|  | Power of motor (W) | 5 | 4 |
|  | Fuse (A) | PCB5A Transformer 0.2A | PCB5A Transformer 0.2A |
|  | Sound (pressure level) dB(A) | ≤58 | ≤58 |
|  | Dimension (W/D/H) (mm) | 1590×238×695 | 1590×238×695 |
|  | Dimension of package (W/D/H) (mm) | 1714×330×830 | 1714×330×830 |
|  | Net weight/gross weight (kg) | 42 | 42 |
| Outdoor Unit | Model | GST60-22L/A(0) | GST60-22R/A(0) |
|  | Compressor Power | 5870 | 5870 |
|  | Compressor Type | Rotary Type | Rotary Type |
|  | LRA(A) | 112 | 112 |
|  | Compressor Overload Protector Type | C-SB373H3A | C-SB373H3A |
|  | Throttle Method | Capillary | Capillary |
|  | Starting Method | Capacitor | Capacitor |
|  | Range of working temperature(℃) | 18℃≤T≤43℃ | -7℃≤T≤43℃ |
|  | Condenser | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф9.52 | ф9.52 |
|  | Row-fin distance (mm) | 3-1.8 | 3-1.8 |
|  | Extended area of heat exchange (I×H×L)mm | 725×1218 | 725×1218 |
|  | Fan motor speed (rpm) | 940 | 940 |
|  | Rated Power of Motor (W) | 92 | 92 |
|  | Fan type-piece | Axial Flow Fan-1 | Axial Flow Fan-1 |
|  | Fan Diameter (mm) | ф450 | ф450 |
|  | Defrosting Method | Auto | Auto |
|  | Sound (pressure level) dB(A) | ≤65 | ≤65 |
|  | Dimension (W/D/H) (mm) | 1250×412×950 | 1250×412×950 |
|  | Dimension of package (W/D/H) (mm) | 1295×450×1110 | 1295×450×1110 |
|  | Net weight/gross weight (kg) | 125/146 | 125/146 |
|  | Refrigerant/Refrigerant Charge (kg) | R22/3.75 | R22/3.75 |
| Connecting Pipe | Length | 5 | 5 |
|  | Outer Diameter | Liquid Pipe | (mm) | Ф12(1/2”) | Ф12(1/2”) |
|  |  | Gas Pipe | (mm) | ф19(3/4”) | ф19(3/4”) |
|  | Max. Distance | Height | (m) | 5 | 5 |
|  |  | Length | (m) | 10 | 10 |

| Model | GST60-38L/A | GST60-38R/A |
| --- | --- | --- |
| Function | Cooling | Cooling | Heating |
| Power (Phase-Frequency-Voltage) | 3Ph 60Hz 380V | 3Ph 60Hz 380V |
| Total Capacity | (W) | 13000 | 13000 | 14500 |
| Rated power | (W) | 6050 | 6050 | 6200 |
| Rated current | (A) | 10.1 | 10.2 | 10.5 |
| Air flow volume | (m3/h) | 2300 | 2300 |
| Dehumidify volume | (L/h) | 1.5 | 1.5 |
| C.O.P/EER | (W/W) | 2.1 | 2.1 | 2.6 |
| Indoor unit | Model | GST60-38L/A(I) | GST60-38R/A(I) |
|  | Fan motor speed (r/min) (H/M/L) | 1300/1200/1100 | 1300/1200/1100 |
|  | Output power of motor(W) | 180 | 180 |
|  | Fan type-piece | Centrifugal Fan-4 | Centrifugal Fan-4 |
|  | Diameter-length (mm) | ф155×175 | ф155×175 |
|  | Evaporator | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф7 | ф7 |
|  | Row-fin distance (mm) | 3-1.6 | 3-1.6 |
|  | Extended area of heat exchange (I×H×L) | 1.34×0.28 | 1.34×0.28 |
|  | Swing motor model | MP35CA | MP35CA |
|  | Power of motor (W) | 4 | 4 |
|  | Fuse (A) | PCB5A Transformer 0.2A | PCB5A Transformer 0.2A |
|  | Sound (pressure level) dB(A) | ≤58 | ≤58 |
|  | Dimension (W/D/H) (mm) | 1590×238×695 | 1590×238×695 |
|  | Dimension of package (W/D/H) (mm) | 1714×330×830 | 1714×330×830 |
|  | Net weight/gross weight (kg) | 42 | 42 |
| Outdoor Unit | Model | GST60-38L/A(0) | GST60-38R/A(0) |
|  | Compressor Power | 5870 | 5970 |
|  | Compressor Type | Rotary Type | Rotary Type |
|  | LRA(A) | 59 | 59 |
|  | Compressor Overload Protector Type | C-SB373H3A | C-SB373H9A |
|  | Throttle Method | Capillary | Capillary |
|  | Starting Method | Capacitor | Capacitor |
|  | Range of working temperature(℃) | 18℃≤T≤43℃ | -7℃≤T≤43℃ |
|  | Condenser | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф9.52 | ф9.52 |
|  | Row-fin distance (mm) | 3-1.8 | 3-1.8 |
|  | Extended area of heat exchange (I×H×L)mm | 725×1218 | 725×1218 |
|  | Fan motor speed (rpm) | 940 | 940 |
|  | Rated Power of Motor (W) | 92 | 92 |
|  | Fan type-piece | Axial Flow Fan-1 | Axial Flow Fan-1 |
|  | Fan Diameter (mm) | ф450 | ф450 |
|  | Defrosting Method | Auto | Auto |
|  | Sound (pressure level) dB(A) | ≤65 | ≤64 |
|  | Dimension (W/D/H) (mm) | 1250×412×950 | 1250×412×950 |
|  | Dimension of package (W/D/H) (mm) | 1295×450×1110 | 1295×450×1110 |
|  | Net weight/gross weight (kg) | 125/146 | 125/146 |
|  | Refrigerant/Refrigerant Charge (kg) | R22/3.95 | R22/3.95 |
| Connecting Pipe | Length | 5 | 5 |
|  | Outer Diameter | Liquid Pipe | (mm) | Ф12(1/2”) | Ф12(1/2”) |
|  |  | Gas Pipe | (mm) | ф19(3/4”) | ф19(3/4”) |
|  | Max. Distance | Height | (m) | 5 | 5 |
|  |  | Length | (m) | 10 | 10 |

| Model | KFR-70DW/NA1(Communication Seat-and-Ceiling Mounted Unit) |
| --- | --- |
| Function | Cooling | Heating |
| Power (Phase-Frequency-Voltage) | 1Ph 50Hz 230V |
| Total Capacity | (W) | 7000 | 8500 |
| Rated power | (W) | 3000 | 3050 |
| Rated current | (A) | 14.6 | 15.1 |
| Air flow volume | (m3/h) | 1170 |
| Dehumidify volume | (L/h) | 2.3 |
| C.O.P/EER | (W/W) | 2.3 | 2.79 |
| Indoor unit | Model | KFR-70D/NA1 |
|  | Fan motor speed (r/min) (H/M/L) | 1360/1280/1240 |
|  | Output power of motor(W) | 100 |
|  | Fan type-piece | Centrifugal Fan-4 |
|  | Diameter-length (mm) | ф125×134 |
|  | Evaporator | Aluminum fin-copper tube |
|  | Pipe diameter | ф7 |
|  | Row-fin distance (mm) | 3-1.6 |
|  | Extended area of heat exchange (I×H×L) | 1.042×0.19 |
|  | Swing motor model | MP35CA |
|  | Power of motor (W) | 4 |
|  | Fuse (A) | PCB5A Transformer 0.2A |
|  | Sound (pressure level) dB(A) | ≤47 |
|  | Dimension (W/D/H) (mm) | 1300×188×600 |
|  | Dimension of package (W/D/H) (mm) | 1414×248×724 |
|  | Net weight/gross weight (kg) | 32/36 |
| Outdoor Unit | Model | KFR-70W/dNA1 |
|  | Input Power | 2900 | 2950 |
|  | Running Current | 14.2 | 14.7 |
|  | Compressor Model | C-RN220H5B |
|  | Compressor Type | Rotary Type |
|  | LRA(A) | 75 |
|  | Compressor Overload Protector Type | Internal Inherent Protector |
|  | Throttle Method | Capillary |
|  | Starting Method | Capacitor |
|  | Range of working temperature(℃) | 7℃≤T≤43℃ |
|  | Condenser | Aluminum fin-copper tube |
|  | Pipe diameter | ф9.52 |
|  | Row-fin distance (mm) | 2-1.8 |
|  | Extended area of heat exchange (I×H×L)mm | 725×813 |
|  | Fan motor speed (rpm) | 60/780 |
|  | Fan type-piece | Axial Flow Fan-1 |
|  | Fan Diameter (mm) | Ф450 |
|  | Defrosting Method | Auto |
|  | Sound (pressure level) dB(A) | ≤58 |
|  | Dimension (W/D/H) (mm) | 950×412×840 |
|  | Dimension of package (W/D/H) (mm) | 1100×450×920 |
|  | Net weight/gross weight (kg) | 75/87 |
|  | Refrigerant/Refrigerant Charge (kg) | R407C/2.5 |
| Connecting Pipe | Length | 5 |
|  | Outer Diameter | Liquid Pipe | (mm) | Ф9.52(3/8”) |
|  |  | Gas Pipe | (mm) | ф16(5/8”) |
|  | Max. Distance | Height | (m) | 5 |
|  |  | Length | (m) | 10 |

| Model | KFR-100DW/NA1-34005 (Communication Seat-and-Ceiling Mounted Unit) | KFR-120DW/NA1-34005 (Communication Seat-and-Ceiling Mounted Unit) |
| --- | --- | --- |
| Function | Cooling | Heating | Cooling | Heating |
| Power (Phase-Frequency-Voltage) | 3Ph - 400V - 50Hz | 3Ph - 400V - 50Hz |
| Total Capacity | (W) | 10000 | 11500 | 12000 | 13000 |
| Rated power | (W) | 4400 | 4400 | 5000 | 4600 |
| Rated current | (A) | 7.5 | 7.5 | 8.3 | 7.8 |
| Air flow volume | (m3/h) | 2100 | 2200 |
| Dehumidify volume | (L/h) | 2.6 | 3.4 |
| C.O.P/EER | (W/W) | 2.27 | 2.61 | 2.4 | 2.83 |
| Indoor unit | Model | KFR-100D/NA1-34005 | KFR-120D/NA1-34005 |
|  | Fan motor speed (r/min) (H/M/L) | 1140/1070/980 | 1110/1000/900 |
|  | Output power of motor(W) | 150 | 150 |
|  | Fan type-piece | Centrifugal Fan-4 | Centrifugal Fan-4 |
|  | Diameter-length (mm) | ф145×175 | ф155×175 |
|  | Evaporator | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф7 | ф7 |
|  | Row-fin distance (mm) | 3-1.6 | 3-1.6 |
|  | Extended area of heat exchange (I×H×L) | 1.34×0.25 | 1.34×0.25 |
|  | Swing motor model | MP35CA | MP35CA |
|  | Power of motor (W) | 4 | 4 |
|  | Fuse (A) | PCB5A Transformer 0.2A | PCB5A Transformer 0.2A |
|  | Sound (pressure level) dB(A) | ≤52 | ≤55 |
|  | Dimension (W/D/H) (mm) | 1590×238×695 | 1590×238×695 |
|  | Dimension of package (W/D/H) (mm) | 1770×330×830 | 1714×330×830 |
|  | Net weight/gross weight (kg) | 42/53 | 42/51 |
| Outdoor Unit | Model | KFR-100W/dNA1-34005 | KFR-120W/dNA1-34004 |
|  | Compressor Model | C-SBN303H8A | C-SBN353H8A |
|  | Input Power | 4250 | 4250 | 4850 | 4450 |
|  | Running Current | 6.9 | 7 | 7.6 | 7.1 |
|  | Compressor Type | Rotary Type | Rotary Type |
|  | LRA(A) | 42 | 55 |
|  | Compressor Overload Protector Type | Internal Inherent Protector | Internal Inherent Protector |
|  | Throttle Method | Capillary | Capillary |
|  | Starting Method | Capacitor | Capacitor |
|  | Range of working temperature(℃) | 2℃≤T≤43℃ | 2℃≤T≤43℃ |
|  | Condenser | Aluminum fin-copper tube | Aluminum fin-copper tube |
|  | Pipe diameter | ф9.52 | ф9.52 |
|  | Row-fin distance (mm) | 2-1.4 | 2-1.8 |
|  | Working Area mm2 | 813×930 | 725×1218 |
|  | Fan motor speed (rpm) | 920 | 840 |
|  | Fan type-piece | Axial Flow Fan-1 | Axial Flow Fan-2 |
|  | Fan Diameter (mm) | Ф482 | Ф450 |
|  | Defrosting Method | Auto | Auto |
|  | Sound (pressure level) dB(A) | ≤62 | ≤63 |
|  | Dimension (W/D/H) (mm) | 1040×410×840 | 1250×950×412 |
|  | Dimension of package (W/D/H) (mm) | 1100×450×880 | 1295×1110×450 |
|  | Net weight/gross weight (kg) | 90/105 | 112/133 |
|  | Refrigerant/Refrigerant Charge (kg) | R407C/3.1 | R407C/3.4 |
| Connecting Pipe | Length | 5 | 5 |
|  | Outer Diameter | Liquid Pipe | (mm) | Ф12(1/2”) | Ф12(1/2”) |
|  |  | Gas Pipe | (mm) | ф19(3/4”) | ф19(3/4”) |
|  | Max. Distance | Height | (m) | 5 | 5 |
|  |  | Length | (m) | 10 | 10 |

| Model | GST36-38R/A |
| --- | --- |
| Function | Cooling | Heating |
| Power (Phase-Frequency-Voltage) | 3Ph 50Hz 380V |
| Total Capacity | (W) | 12000 | 13500 |
| Nominal Power | (W) | 5050 | 5000 |
| Rated power | (W) | 5937 | 5051 |
| Rated current | (A) | 8.38 | 8.17 |
| Air flow volume | (m3/h) | 2500 |
| Dehumidify volume | (L/h) | 2.6 |
| C.O.P/EER | (W/W) | 2.4 | 2.893 |
| Indoor unit | Model | KFR-120D/B1-G |
|  | Fan motor speed (r/min) (H/M/L) | 1100/1000/900 |
|  | Output power of motor(W) | 150 |
|  | Fan Motor Capacitor | 5 |
|  | Fan type-piece | Cross flow fan-1 |
|  | Diameter-length (mm) | ф155×175 |
|  | Evaporator | Aluminum fin-copper tube |
|  | Pipe diameter | ф7 |
|  | Row-fin distance (mm) | 3-1.6 |
|  | Extended area of heat exchange (I×H×L) | 1.34×0.25 |
|  | Swing motor model | MP35CA |
|  | Power of motor (W) | 4 |
|  | Fuse (A) | PCB5A Transformer 0.2A |
|  | Sound (pressure level) dB(A) | 50.2/50.1/49.3 |
|  | Dimension (W/D/H) (mm) | 1590×238×695 |
|  | Dimension of package (W/D/H) (mm) | 1714×415×830 |
|  | Net weight/gross weight (kg) | 42/53 |
| Outdoor Unit | Model | KFR-120W/dB1-G |
|  | Compressor Model | C-SB373H8A |
|  | Compressor Type | Rotary Type |
|  | LRA(A) | 55 |
|  | Compressor Overload Protector Type | Internal Inherent Protector |
|  | Throttle Method | Capillary |
|  | Starting Method | Capacitor |
|  | Range of working temperature(℃) | -2℃≤T≤43℃ |
|  | Condenser | Aluminum fin-copper tube |
|  | Pipe diameter | ф9.52 |
|  | Row-fin distance (mm) | 2-1.8 |
|  | Extended area of heat exchange (I×H×L)mm | 813×930 |
|  | Fan motor speed (rpm) | 840/740/640 |
|  | Rated Power of Motor (W) | 68 |
|  | Fan Motor Capacitor (μF) | 3.5 |
|  | Air Flow Volume of Outdoor Unit | 5000 |
|  | Fan type-piece | Axial Flow Fan-1 |
|  | Fan Diameter (mm) | ф482 |
|  | Defrosting Method | Auto |
|  | Sound (pressure level) dB(A) | ≤62 |
|  | Dimension (W/D/H) (mm) | 1040×410×840 |
|  | Dimension of package (W/D/H) (mm) | 1295×450×1110 |
|  | Net weight/gross weight (kg) | 90/105 |
|  | Refrigerant/Refrigerant Charge (kg) | R22/3.95 |
| Connecting Pipe | Length | 5 |
|  | Outer Diameter | Liquid Pipe | (mm) | Ф12(1/2”) |
|  |  | Gas Pipe | (mm) | ф19(3/4”) |
|  | Max. Distance | Height | (m) | 5 |
|  |  | Length | (m) | 10 |

Component Name

Applicable to 70 & 100 unit

Indoor unit	Swing Assy.

Air outlet

Decorative panel

Air inlet		Water outlet

Front grill

Remote controller

Outdoor Unit

Air outlet

Connecting pipe

Air outlet grill

Drainage pipe

Air outlet

Applicable to 120 unit

Indoor unit

Swing Assy.     Air outlet

Decorative panel

Air inlet		Water outlet

Front grill

Remote controller

Outdoor Unit

Air outlet grill

Air outlet

Connecting pipe

Air outlet grill

Air outlet

Drainage pipe

Overall and Installing Dimension

Overall and Installing Dimension of Indoor Unit

Applicable to KFR-70DE/B1  GST24-22L/A  GST24-22R/A

Overall dimension

Installing dimension

Applicable to all except KFR-70D/B1  GST24-22L/A  GST24-22R/A

Overall and Installing Dimension of Outdoor Unit

Applicable to 70 & 100 unit

Unit: mm

Bolt

Nut

Wrench

Applicable to 120 unit

Unit: mm

Bolt

Nut

Wrench

System Diagram

System Diagram for Cooling-and-Heating Unit

Capillary

4-way valve

Evaporator	 Condenser

Gas-liquid

Cooling     separator	Compressor

Heating

Switch on the power to start the unit. Low-pressure refrigerant vapor from evaporator is absorbed into the compressor, where it is compressed into high-temp. and high-pressure gas. The gas refrigerant is then diverted to condenser, where it is liquidized after heat exchange with outdoor air. After that, the liquidized refrigerant flows through capillary for decrease of temperature and pressure and then enters into evaporator, where it becomes low-temp. and low-pressure refrigerant vapor after heat exchange with indoor air to be regulated. This process is repeated in cycle to achieve the purpose of cooling. (Under heating mode, the 4-way valve will change the flow of refrigerant, so that the condenser absorbs heats and the evaporator gives out heats, thus to achieve the purpose of heating).

Electrical Diagram

(Communication Seat-and-Ceiling Mounted Unit)

(Communication Seat-and-Ceiling Mounted Unit)

(Communication Seat-and-Ceiling Mounted Unit)

In case of any change in the Electrical Diagram shown above, please follow the drawing on cabinet.

# Controller and Remote Controller Function Manual and Operating Instructions

Controller and Remote Controller Function Manual

7.1.1 Temperature Parameters

- Indoor preset temperature (Tpreset)

- Indoor ambient temperature (Tamb.)

- Outdoor condenser temperature (Tcond.)

7.1.2　Basic Functions

Once started under any mode, the compressor will not be stopped within 6 minutes with the change of ambient temperature. Once stopped, it cannot be restarted unless after 3-minute lag.

7.1.2.1　Cooling Mode

- When Tamb.≥Tpreset+1℃, the unit will run under cooling mode, in which case the compressor and outdoor fan will be started, the indoor fan will run at preset speed and the swing will run as preset.

- When T amb.≤Tpreset -1℃, the compressor and outdoor fan will be stopped and the indoor fan will run at preset speed.

- When Tpreset -1℃<T amb.< Tpreset +1℃, the unit will maintain its original operating status.

- Under cooling mode, the temperature can be set within a range from 16 to 30℃. The initial value is 25℃.

Tamb

Start cooling

Maintain original operating status

6 min.       3 min.         6 min.            Stop cooling

Compressor

Outdoor fan

Indoor fan	Run at preset speed

Run                        Stop

7.1.2.2 Dehumidifying Mode

- When T amb.≥Tpreset +2℃, the unit will run under cooling mode, in which case the compressor and outdoor fan will be started, the indoor fan will run at low speed.

- When Tpreset -2℃≤T amb.≤Tpreset +2℃, the compressor, indoor unit and outdoor unit will run 6 minutes and stop 4 minutes in repeated cycle, while the indoor fan will run at low speed.

- When T amb.< Tpreset -2℃, the compressor and outdoor fan will be stopped, and the indoor ran will keep running at low speed.

- Under dehumidifying mode, the temperature can be set within a range from 16 to 30℃. The initial value is 25℃.

Tamb

Start cooling

Run under dehumidifying mode

6 min.   4 min.  6 min.  4 min.                 Stop cooling

Compressor

Outdoor fan

Indoor fan	Low speed

Run                        Stop

7.1.2.3 Heating Mode

- When T amb.≤Tpreset -1℃, the unit will run under heating mode, in which case the switchover valve, compressor and outdoor fan will be started, while the indoor fan will run at preset speed under preset cold air prevention condition.

- If T amb.≥Tpreset +1℃, the compressor and outdoor fan will be stopped, the switchover valve is still energized and the indoor fan will run at low speed for 10 seconds before it is stopped.

- When Tpreset -1℃<T amb.< Tpreset +1℃, the unit will maintain its original operating status.

  - Under heating mode, the temperature can be set within a range from 16 to 30℃. The initial value is 25℃.

  - If the unit is switched off under heating mode or switched to another mode, the 4-way valve will be de-energized 2 minutes after the compressor is stopped.

Start cooling

Ambient temperature  Tamb

Maintain original operating status

6 min.       3 min.           6 min.            Stop cooling

Compressor

Outdoor fan

Indoor fan    ≤5 minutes Preset speed	≤5 minutes  Preset speed

Louver valve

Run                        Stop

7.1.2.3.1 Cold Air Prevention Condition

The compressor will start to run under heating mode and the indoor fan will not run. After 5 minutes or if the outlet temperature is high, the indoor fan will run at preset speed. The indoor fan will no longer be stopped once it is started. Once running at preset speed, the indoor fan will no longer be switched back to low speed compulsively.

7.1.2.3.2 Defrosting Conditions

- When the condenser is detected to have frost, the system will enter into defrosting mode, in which case the switchover valve, indoor fan and outdoor fan will be stopped.

- When it is detected that the frost in condenser is completely eliminated, the switchover valve and outdoor fan will be started simultaneously, while the indoor fan will start to run under preset cold air prevention condition.

≤10 min.

Compressor

Outdoor fan

Indoor fan                                         ≤3min.  Preset speed

Run                             Stop

7.1.2.4 Fan Mode

Indoor fan will run at preset speed

Auto Speed	Low Speed	Medium Speed	High Speed

The temperature can be set within a range from 16 to 30℃. The initial value is 25℃.

7.1.2.5 Auto Mode

Under this mode, the system will automatically select its run mode (cooling, dehumidifying, heating or fan) with the change of ambient temperature.

  - Once a mode is started, the unit will run at least 30 seconds before it can the run status under auto mode according to the ambient temperature.

7.1.3 AUTO ON/OFF and Sleep Function

7.1.3.1 Sleep

- If the controller is under cooling or dehumidifying mode, the preset temperature will be increased by 1℃ one hour after running under sleep mode and will be increased by another 1℃ after two hours. The temperature will increased by 2℃ within two hours. After that, the unit will run at this temperature.

Set the Temperature Tpreset

1 hours	2 hours	Over 2 hours

- If the controller is under heating mode, the preset temperature will be decreased by 1℃ one hour after running under sleep mode and will be decreased by another 1℃ after two hours. The temperature will decreased by 2℃ within two hours. After that, the unit will run at this temperature.

1 hours	2 hours	Over 2 hours

Set the Temperature Tpreset

- No sleep function under fan mode or auto mode.

7.1.3.2 AUTO ON

- You can set AUTO ON function when the unit is under standby status. Upon the time of AUTO ON, the controller will run under preset mode. The time interval for AUTO ON is 0.5h, and can be set within 0.5 - 24 hours.

7.1.3.3 AUTO OFF

- You can set AUTO OFF function when the unit is under ON status. Upon the time of AUTO OFF< the system will be switched off. The time interval for AUTO OFF is 0.5h, and can be set within 0.5 - 24 hours.

7.1.4 Other Control

7.1.4.1 Swing Control

You can switch on or off the swing by pressing the SWING key. The swing is valid only when the indoor fan is running.

7.1.4.2 Buzzer Control

When the controller is energized or receives valid key-press signal, the buzzer will give out musical beep.

7.1.4.3 Automatic Control of Indoor Fan Speed

Under this mode, the indoor fan will automatically select its speed, i.e. high, medium or low, with the change of ambient temperature. Once a speed is activated, the indoor fan will run at least 30 seconds before it can switch per aforementioned conditions.

7.1.5 Protection

7.1.5.1 Indoor Antifreeze Protection

- If E2 is displayed under cooling mode, the compressor, outdoor fan and indoor fan will be stopped, and the swing motor will maintain its original status. When evaporator temperature is higher than 6℃ and the compressor has been stopped for 4 minutes, the display will resume and the controller will run under preset mode.

- Under dehumidifying mode (i.e. run 6 minutes and stop 4 minutes), if it is detected within 3 minutes successively that the tube temperature is lower than -2℃ after the compressor has been running for 3 minutes, the compressor and outdoor unit will be stopped, the indoor fan will run at low speed, and E2 will be displayed. When tube temperature higher than 6℃ and the compressor has been stopped for 4 minutes, the display will resume and the controller will run under preset mode.

7.1.5.2 Compressor High-pressure Protection

If high-pressure protection is detected within 3 seconds successively, all loads will be closed, all key-press and remote control signals will be shielded, and E1 will be displayed. When it is detected within 6 seconds successively that the compressor has released high-pressure protection, shielding of key-press signal will be removed but E1 will be still displayed. To clear off E1 display, you have to press ON/OFF key to switch off the unit and press it again to restart.

7.1.5.3 Compressor Low-pressure Protection

- When it is detected that the low-pressure switch is off, the complete unit will be stopped and be automatically restarted after 3 minutes. If E3 is displayed, the unit cannot be restarted automatically, in which case you have to press ON/OFF key to switch off the unit and press this key again to restart.

- If it is detected that the low-pressure switch is off when the compressor is stopped, the complete unit will be stopped, E3 will be displayed and the unit cannot be restarted automatically. You have to press ON/OFF key to switch off the unit and press this key again to restart.

7.1.5.4 Exhaust Pipe High-temp. Protection

- After the compressor is started, if the exhaust temperature is too high or exhaust sensor is in short circuit (or open circuit), the unit will be stopped when the indoor ambient temperature reaches the preset value.

- After the compressor is stopped for 3 minutes, the complete unit will be restarted when the exhaust temperature is resumed to normal.

- In case of aforementioned phenomena, the complete unit cannot resume its operation and E4 will be displayed. You have to press ON/OFF key to switch off the unit and press this key again to resume operation under preset mode.

7.1.5.5 Indoor Overtemperature Protection

- If it is detected that the evaporator tube temperature is too high under heating mode, the outdoor fan will be stopped. When the evaporator tube temperature resumes to normal, the outdoor fan will be started.

7.1.5.6 Low-voltage Protection

- If the current is detected over 22A as the compressor is started, the unit will be stopped when indoor ambient temperature reaches preset value. The compressor will automatically resume to its original operating status after it is stopped for 3 minutes. If E5 is displayed, the compressor cannot resume to its original operating status automatically, in which case you have to press ON/OFF key to switch off the unit and press this key again.

7.1.5.7 Fault Code and Definition

| Fault Code | Definition |
| --- | --- |
| E1 | Compressor High-pressure Protection |
| E2 | Indoor Antifreeze Protection |
| E3 | Compressor Low-pressure Protection |
| E4 | Exhaust Pipe High-temp. Protection |
| E5 | Low-voltage Protection |

7.1.5.8 Compulsive Cooling (Heating) Mode

If no valid key-press upon first energization:

- From the remote controller, you can press temperature selection key (+) to enter into compulsive heating mode, in which case all the keys on front panel and remote controller will be shielded, all loads will be started and the indoor fan will run at high speed. If it is detected that ambient temperature is in open circuit or higher than 105℃, or that evaporator temperature is in open circuit or higher than 105℃, the buzzer will beep. After five minutes, the unit will be stopped and enter into normal standby status.

- From the remote controller, you can press temperature selection key (1) to enter into compulsive cooling mode, in which case all the keys on front panel and remote controller will be shielded, all loads except the 4-way valve will be started and the indoor fan will run at high speed. If it is detected that ambient temperature is in open circuit or higher than 105℃, or that evaporator temperature is in open circuit or higher than 105℃, the buzzer will beep. After five minutes, the unit will be stopped and enter into normal standby status.

The functions stated in ① and ② are only for test purpose. Compulsive heating function is not available for cooling-only unit.

7.1.5.9 Indicator

- Power indicator: It is bright when energized and black when de-energized. It will blink under indoor antifreeze protection, compressor high-pressure protection, low-voltage protection and defrosting.

- Cooling indicator: It is bright under cooling mode, dehumidifying mode, auto cooling mode or auto dehumidifying mode. It is black under other modes.

- Heating indicator: It is bright under heating mode and auto heating mode. It is black under other modes

7.1.5.10 Power-OFF Memory Function

What is memorized includes the mode, swing, preset temperature, preset fan speed, Auto ON/OFF (If the power is cut off before the preset time for AUTO ON/OFF, the timer will count the time again once the power is resumed. If the power is cut off after the preset time for AUTO ON/OFF, the unit, once energized again, will run under the mode after preset AUTO OFF time).

Once energized again after any de-energization, the unit can be automatically restarted according to the memory.

Description and Function of Remote Controller Keys

Notes:

- Make sure that there is no obstruction between remote controller and signal receiving window.

- Do not fall off or throw the remote controller.

- Do not let any liquid flow into remote controller, or expose the remote controller under direct sunshine or extreme hot temperature.

Description and Function of Remote Controller Keys (After opening the rear cover)

Note: This remote controller is for general use and applicable to multiple types (functions) of air conditioner.

Please understand that the keys not applicable to this air conditioner will not be described herein.

Installation of Remote Controller Batter

- Operating Guideline

General Procedures:

- Switch on the power and press ON/OFF key to start the air conditioner.

- Press MODE key to select your desired run mode.

- Press SWING key to enable the guide louver to swing at a specific angle. Press it again to stop the swing.

- Press FAN key to set the fan speed.

- Press +/- key to set your desired temperature.

Optional Procedures:

- Press SLEEP key from remote controller to set the sleep mode.

- Press AUTO ON/OFF key and then press +/- key to set the timer.

Note: When auto mode is selected, the air conditioner will automatically select an appropriate run mode according to the indoor temperature, making the environment comfortable.

- Replacement of Remote Controller Battery

Two pieces of 7# alkali dry batteries are used in the remote controller.

1. Slide the battery cover of remote controller downward. Remove the old batteries and replace with two pieces of new batteries (Take care that the polarity shall be correct)

2. Close the battery cover of remote controller.

Note:

- Do not use new batteries together with old batteries, or use different types of batteries together.

- To avoid leakage of liquid and damage to the remote controller, please take out the batteries if you will not use the remote controller in several weeks.

- Operate the remote controller within effective range.

- Keep the remote controller at least 1 meter away from television set or sound equipment.

RESET key

Insert two 7# batteries.

Disassembly and Assembly Procedures

Disassembly Procedures of Indoor Unit

Applicable Unit Models:

Disassemble Front Grill Sub-Assy

Manually push the clasp of front grill sub-assy downward to open the front grill. (Fig 8-1)

(Fig 8-1)

Clasp

Disassemble Left and Right Decorative Panels

Use screwdriver to screw off the screws shown in the position, and then move the panels toward the direction of arrow to Disassemble the left and right decorative panels. (Fig 8-2)

Screw

(Fig 8-2)

Disassemble Electric Box Assy

- Use screwdriver to twist off the two screws shown in the figure and remove the electric box cover (8-3);

- Use screwdriver to twist off the screw shown in the figure, remove the capacitor support, and disconnect the cables (refer to Figure 8-4);

- Use screwdriver to twist off the four screws (2 screws at each side), remove the electric box sub-assy, and disconnect the cables (refer to Figure 8-5);

(Fig 8-4)     Screw      Screw  (Fig 8-5)

| Operating Procedures / Photos |  |
| --- | --- |
| Disassemble Front Panel Assy |
| Use screwdriver to screw off the six screws shown in the figure (two screws at the left, right and rear sides respectively), remove the front panel assy toward the direction shown in the figure to remove it (refer to figures 8-6, 8-7). | Screw Screw (Fig 8-6) (Fig 8-7) |
| Disassemble Guide Louver Sub-assy |
| First remove the guide louver from the fitting position of the guide louver support, then remove the two ends of the guide louver from the fitting position of the swing motor. (Fig 8-8) | Support Motor fitting position (Fig 8-8) |
| Disassemble Water Tray Sub-assy |
| Use screwdriver to screw off the three screws shown in the figure so as to remove the water tray sub-assy (refer to Figure 8-9). | Screw (Fig 8-9) |

| Operating Procedures / Photos |  |
| --- | --- |
| Disassemble Mounting Plate Sub-assy of Swing Louver |
| Use screwdriver to screw off the screws at both ends of the mounting plate sub-assy of swing louver. Take the mounting plate sub-assy of swing louver apart from the guide louver support. (Fig 8-10) | Screw Support (Fig 8-10) |
| Disassemble Evaporator Assy |
| Use screwdriver to screw off the screw shown in the figure. Remove the tube-exit clamp sub-assy of evaporator. (Fig 8-11) Use screwdriver to screw off the screw shown in the figure and remove the evaporator assy. Handle with care. (Fig 8-12、Fig 8-13) | (Fig 8-11) Screw Screw (Fig 8-12) Screw (Fig 8-13) |
| Disassemble Air Outlet Rear Side Plate Sub-assy |
| First remove the flocking fabrics and the left and right side plate cushions at the air outlet; then use screwdriver to screw off the screw shown in the figure. (Fig 8-14) | Screw (Fig 8-14) |

| Operating Procedures / Photos |  |
| --- | --- |
| Disassemble Mounting Plate Sub-assy of Swing Motor |
| Use screwdriver to screw off the screw shown in the figure. (Fig 8-15) | (Fig 8-15) Screw |
| Disassemble Left and Right Side Plate Foam Sub-ass |
| Follow the shown direction to remove the left and right side plate foam sub-assy. (Fig 8-16) | Left Side Plate Foam Sub-assy | Right Side Plate Foam Sub-assy |
|  | (Fig 8-16) |
| Disassemble Fan Motor Assy |
| Press downward the clasps fitting the front and rear propeller housings, then pull upward to remove the front propeller housing (refer to Figure 8-17). Hold the clasp position of the rear propeller housing and pull upward to remove the rear propeller housing (refer to Figure 8-18). Use special tool to screw off the two holding screws at the coupling, move the coupling toward the fan until the coupling and shaft sub-assy can be removed; use special tool to remove the holding screw fixing the fan to remove the fan (refer to Figure 8-19). | Clasp Position (Fig 8-17) Holding Screw (Fig 8-18) (Fig 8-19) |

| Operating Procedures / Photos |  |
| --- | --- |
| Disassemble Bearing Mounting Plate |
| Use screwdriver to screw off the four screws at the bearing mounting plate. (Fig 8-20) | Screw (Fig 8-20) |
| Disassemble Motor |
| Use screwdriver to screw off the screw shown in the figure to remove the motor clamp and the motor fixing hoop. (Fig 8-20) | Screw (Fig 8-20) |
| Disassemble Motor Mounting Plate Sub-assy |
| Use screwdriver to screw off the screw at the motor mounting plate to remove the motor mounting plate sub-assy. (refer to Figure 8-21). | Motor Mounting Plate Sub-assy Screw (Fig 8-21) |

| Operating Procedures / Photos |  |
| --- | --- |
| Disassemble Supporting Plate of Motor Support |
| Use screwdriver to screw off the screws connecting the supporting plate of motor support and the rear side plate sub-assy with the motor support. (Fig 8-22) | Tapping Screw (Fig 8-22) |
| Disassemble Left and Right Mounting Plates |
| Use tool to remove the bolts (2 X M8, 2 X M6) fixing the left and right mounting plates. (Fig. 8-23) | Mounting Plate M8 Bolt M6 Bolt (Fig 8-23) |
| Disassemble Motor Support |
| Use screwdriver to screw off the screws at the rear support base plate and at the both sides of the support as shown in the figure to remove the motor support. (refer to Fig. 8-24、8-25). | (Fig 8-24) Screw (Fig 8-25) |

| Disassembly Procedures of Indoor Unit |
| --- |
| Operating Procedures / Photos Applicable to all unit models except （KFR-70D/B1） |
| Disassemble Front Grill Sub-Assy |
| Use tool to push the clasp 1 of front grill sub-assy downward to open the front grill. (Fig 8-26) | Front Panel Clasp 1 (Fig 8-26) |
| Disassemble Left and Right Decorative Panels |
| Screw off the screw in the decorative panel, and then manually pull toward the direction of arrow to remove the left and right decorative panels. (Fig 8-27) | Screw (Fig 8-27) |
| Disassemble Electric Box Assy |
| Use screwdriver to twist off the two screws at the electric box and manually pull the electric box cover upward to remove the electric box. (Fig 8-28) Use screw driver to loosen the two screws at upper and two screws at lower. Remove the capacitor board (As shown in Fig. 8-29) Use screwdriver to twist off the two upper screws and the two lower screws and remove the capacitor support. Use screwdriver to screw off the screw shown in Figure 5 and disconnect the cables to remove the electric box sub-assy. (Fig 8-30) | Screw (Fig 8-28) Screw (Fig 8-29) Screw (Fig 8-30) |

| Operating Procedures / Photos |  |
| --- | --- |
| Disassemble Front Panel Assy |
| Screw off the screws at the front and at the two sides. Remove the front panel sub-assy. (Fig 8-31) | Front Panel Sub-assy Screw (Fig 8-31) |
| Disassemble Guide Louver Sub-assy |
| First remove the guide louver from the fitting position of the guide louver support, then remove the two ends of the guide louver from the fitting position of the swing motor. (Fig 8-32) | (Fig 8-32) |
| Disassemble Water Tray Sub-assy |
| Use screwdriver to screw off the nut with washer at the middle of water tray. (Fig 8-33) Use screwdriver to screw off the two side screws of the auxiliary water tray. Pull the auxiliary water tray and the water tray upward to remove them. (Fig 8-34) | Water Tray Nut with Washer (Fig 8-33) Auxiliary Water Tray Screw (Fig 8-34) |
| Disassemble Mounting Plate Sub-assy of Swing Louver |  |
| Use screwdriver to screw off the screws at both ends of the mounting plate sub-assy of swing louver. Take the mounting plate sub-assy of swing louver apart from the guide louver support. (Fig 8-35) | Screw (Fig 8-35) |

| Operating Procedures / Photos |  |
| --- | --- |
| Disassemble Evaporator Assy |
| Use screwdriver to screw off the two screws at the tube-exit plate of evaporator. Remove the tube-exit plate of evaporator. (Fig 8-36) Use screwdriver to screw off the screw shown in the figure to remove the evaporator. (Fig 8-37) | Tapping Screw Tube-exit Plate of Evaporator ) Tapping Screw |
| Disassemble Left and Right Mounting Plates | (Fig 8-37) |
| First remove the flocking fabrics and the left and right side plate cushions at the air outlet; then use screwdriver to screw off the screw shown in the figure. (Fig 8-38) | Screw (Fig 8-38) |
| Disassemble Mounting Plate Sub-assy of Swing Motor |
| Use screwdriver to screw off the screw shown in the figure. (refer to Figure 8-39). | Screw (Fig 8-39) |

| Operating Procedures / Photos |  |
| --- | --- |
| Disassemble Mounting Plate Sub-assy of Swing Motor |
| Use screwdriver to screw off the screw shown in the figure. (Fig 8-40) | Left Side Plate Foam Sub-assy | Right Side Plate Foam Sub-assy |
|  | (Fig 8-40) |
| Disassemble Fan Motor Assy |  |
| Press downward the clasps fitting the front and rear propeller housings, then pull upward to remove the front propeller housing (refer to Figure 8-41). Hold the clasp position of the rear propeller housing and pull upward to remove the rear propeller housing (refer to Figure 8-42). Use special tool to screw off the two holding screws at the coupling, move the coupling toward the fan until the coupling and shaft sub-assy can be removed; use special tool to remove the holding screw fixing the fan to remove the fan (refer to Figure 8-43). |  |
|  | (Fig 8-41) (Fig 8-42) Clasp Position Holding Screw Clasp Position |
| Disassemble Bearing Mounting Plate |
| Use screwdriver to screw off the four screws at the bearing mounting plate. (Figure 8-44). Disassemble Motor Use screwdriver to screw off the screw shown in the figure to remove the motor clamp and the motor fixing hoop.(Figure 8-45) | Screw Screw (Fig 8-44) (Fig 8-45) |

| Operating Procedures / Photos |  |
| --- | --- |
| Disassemble Motor Mounting Plate Sub-assy |
| Use screwdriver to screw off the six screws at the motor mounting plate to remove the motor mounting plate sub-assy. (Fig 8-46) | Motor Mounting Plate Sub-assy (Fig 8-46) Tapping Screw |
| Disassemble Supporting Plate of Motor Support |
| Use screwdriver to screw off the screws connecting the supporting plate of motor support and the rear side plate sub-assy with the motor support. (Fig 8-47) Disassemble Left and Right Mounting Plates | Tapping Screw (Fig 8-47) |
| Use tool to remove the bolts (2 X M8, 2 X M6) fixing the left and right mounting plates. (Fig 8-48) Disassemble Motor Support Use screwdriver to screw off the screws at the rear support base plate and at the both sides of the support as shown in the figure to remove the motor support. | (Fig 8-48) Right Mounting Plate Bolt Left Mounting Plate Tapping Screw Bolt (Fig 8-49) |

| Disassembly Procedures of Outdoor Unit |
| --- |
| Operating Procedures / Applicable Unit Models: （70、100） |
| Disassemble Front Side Plate |
| Screw off the four screws around the front side plate to remove the front side plate. (Fig 8-50) | Front side plate Screw (Fig 8-50) |
| Disassemble Top Cover |
| Screw off the tapping screws around the top cover, and then pull the top cover upward to remove it. (Fig 8-51) | Screw Top Cover (Fig 8-51) |
| Disassemble Rear Grill |
| Screw off the four screws around the rear grill to remove the rear grill. (Fig 8-52) | Screw Rear Grill (Fig 8-52) |

| Operating Procedures / Photos |
| --- |
| Disassemble Cabinet |
| Use screwdriver to screw off the screws around the cabinet to remove the cabinet. (Fig 8-53) | Screw Cabinet. (Fig 8-53) |
| Disassemble Electric Box | Screw |
| Use screwdriver to screw off the screws fixing the electric box, and pull the electric box to remove it. (Fig 8-54) | Electric Box Communication Ceiling Type Unit Electric Box Screw (Fig 8-54) |
| Disassemble Right Side Plate |
| Use screwdriver to screw off the screws at the right side plat, condenser side plate, gas valve and liquid valve, and then pull the right side plate sub-assy upward to remove it. (Fig 8-55) | Screw Right Side Plate (Fig 8-55) |

| Operating Procedures / Photos |
| --- |
| Disassemble Axial Flow Fan |
| Use spanner to remove the nut at the fan to remove the axial flow fan. (Fig 8-56) | Nut Axial Flow Fan (Fig 8-56) |
| Disassemble Outdoor Motor | Motor |
| Screw off the four tapping screws fixing the motor, pull out the motor lead-out cable plug, and remove the motor. Screw off the two tapping screws fixing the motor support, and pull the motor support upward to remove it. (Fig 8-57) | Screw Fixing the Motor Motor Cable Motor Support Fixing Screw (Fig 8-57) |
| Disassemble 4-Way Valve |
| （Only Heating and Cooling Unit has such valve） Screw off the holding nut of the 4-way valve coil and remove the coil. Use wet cotton cloth to wrap the 4-way valve, unsold the four soldering points connecting the 4-way valve, and remove the 4-way valve. Be quick during the unsoldering process, pay attention to keep the wrapping cloth wet and do not allow the soldering flame to burn the compressor lead-out cable. (Fig 8-58) | 4-Way Valve Soldering Point (Fig 8-58) |

| Operating Procedures / Photos |
| --- |
| Disassemble Capillary |
| Unsold the soldering points at the capillary, the valve and the condenser to remove the capillary. Pay attention not to allow the soldering slag to block the capillary. (Fig 8-59) | Capillary |
| Disassemble Valve |  |
| Unscrew the two screws fixing the gas valve, unsolder the soldering point between the gas valve and the return-air duct and remove the gas valve (note: when unsoldering the soldering point, use wet cloth to completely wrap the gas valve to prevent valve body from being harmed by high temperature). Unscrew the two screws fixing the liquid valve, unsolder the soldering point connecting the liquid valve and the fork type pipe, and remove the liquid valve. (Fig 8-60) | Liquid Valve Screw Gas Valve |
| Disassemble Compressor |
| Firstly unsolder the pipes connecting the compressor, and then unscrew the three foot nuts at the compressor to remove the compressor. (Fig 8-61) | Foot Nut |

| Disassembly Procedures of Outdoor Unit |
| --- |
| Operating Procedures |
| Disassemble Rear Grill |
| Screw off the tapping screws at the rear side plate, valve support chassis and condenser side plate to remove the rear grill. (Fig 8-62) | Rear Grill Screw |
| Disassemble Top Cover Plate Screw |
| Screw off the tapping screws around the top cover, and then pull the top cover upward to remove it. (Fig 8-63) | Top Cover |
| Disassemble Front Side Plate |
| Screw off the three tapping screws at the front side plate, and then pull the front side plate upward to remove it. (Fig 8-64) | Front Side Plate Screw |

| Operating Procedures / Photos |
| --- |
| Disassemble Cabinet |
| Unscrew the screws around the cabinet to remove the cabinet. (Fig 8-65) | Screw Cabinet |
| Disassemble Electric Box |  |
| Unscrew the screws around the electric box sub-assy to remove it. (Fig 8-66) | Screw Communication Cassette Type Unit Electric Box Screw |
| Disassemble Right Side Plate |
| Unscrew the screws around the right side plate to remover the right side plate. (Fig 8-67) | Right Side Plate Screw |

| Operating Procedures / Photos |
| --- |
| Disassemble Axial Flow Fan |
| Use spanner to twist off the nut of the fan and remove the fan. (Fig 8-68) | Nut Nut |
| Disassemble Outdoor Motor |  |
| Screw off the four tapping screws fixing the motor, pull out the motor lead-out cable plug, and remove the motor. Screw off the two tapping screws fixing the motor support, and pull the motor support upward to remove it. (Fig 8-69) | Motor Screw Fixing the Motor Motor Support Fixing Screw |
| Disassemble 4-Way Valve |
| Screw off the holding nut of the 4-way valve coil and remove the coil. Use wet cotton cloth to wrap the 4-way valve, unsold the four soldering points connecting the 4-way valve, and remove the 4-way valve. Be quick during the unsoldering process, pay attention to keep the wrapping cloth wet and do not allow the soldering flame to burn the compressor lead-out cable. (Fig 8-70) | 4-Way Valve |

| Operating Procedures / Photos |
| --- |
| Disassemble Valve |
| Unscrew the screw fixing the valve, unsolder the connecting pipe of the valve, and remove the valve. (Fig 8-71) | Screw Liquid Valve Screw Gas Valve |
| Disassemble Capillary |  |
| Unsolder the soldering points between the capillary and other pipes to remove the capillary. (Fig 8-72) | Capillary |
| Disassemble Compressor |
| Unscrew the foot screw of the compressor and unsolder the connecting pipe to remover the compressor. (Fig 8-73) | Foot Nut |

Exploded View and Components and Parts List

Exploded View of Components and Parts of Indoor Unit

| Components and Parts List of Indoor Unit |
| --- |
| No. | Description | Part Code | Qty |
|  |  | KFR-70D/B1 |  |
| 1 | Left Decorative Plate of Guide Plate Extruded Plastic Bar | 26112417 | 1 |
| 2 | Guide Louver I | 10512025 | 2 |
| 3 | Mounting Plate of Swing Louver | 01332424 | 1 |
| 4 | Guide Louver Holder | 24212020 | 3 |
| 5 | Guide Louver Support | 24222016 | 2 |
| 6 | Guide Louver | 10512407 – ошибка | 1 |
| 7 | Guide Louver II | 10512025 | 2 |
| 8 | Right Decorative Plate of Guide Plate Extruded Plastic Bar | 26112421 | 1 |
| 9 | Mounting Plate (Left) of Swing Motor | 26152007 | 1 |
| 10 | Front Panel Sub-Assy | 01532414 | 1 |
| 11 | PCB Mounting Box | 20102138 | 1 |
| 12 | Display Board | 30292701 | 1 |
| 13 | Button Front Panel Sub-assy | 20162004 | 1 |
| 14 | Right Mounting Plate of Swing Motor | 26152408 | 1 |
| 15 | Stepping Motor (Air Guide) MP35CA | 15212402 | 2 |
| 16 | Swing Motor Clamp | 26112026 | 4 |
| 17 | Water Tray | 01272411 | 1 |
| 18 | Auxiliary Water Tray | 01272403 | 1 |
| 19 | Pipe Clip | 70812001 | 1 |
| 20 | Drainage Pipe Sub-assy | 05235433 | 1 |
| 21 | Handle | 26232001 | 4 |
| 22 | Right Side Plate Foam | 12312408 | 1 |
| 23 | Right Mounting Plate | 01332404 | 1 |
| 24 | Motor Bearing Block | 01792408 | 2 |
| 25 | Supporting Plate of Motor Support | 01792409 | 1 |
| 26 | Right Decorative Plate | 26112033 | 1 |
| 27 | Tube-exit Clamp of Evaporator | 01072424 | 1 |
| 28 | Electric Box Assy | 01403242 | 1 |
| 29 | Wire Seat | 24253001 | 1 |
| 30 | Wire-pressed Clamp | 24253002 | 1 |
| 31 | Terminal Board RS9413G | 42010178 | 1 |
| 32 | Fuse 5A 250VAC VDE | 46010013 | 1 |
| 33 | Mainboard 6152J | 30036052 | 1 |
| 34 | Ring of Bearing | 76512404 | 2 |
| 35 | Fan Bearing | 76512210 | 2 |
| 36 | Power Transformer SC28D | 43110194 | 1 |
| 37 | Electric Box Cover | 01413008 | 1 |
| 38 | Centrifugal Fan | 10312401 | 4 |
| 39 | Shaft Assy | 73012401 | 2 |
| 40 | Capacitor CBB61 3μF/450V | 33010027 | 1 |

| 41 | Capacitor Support | 01722408 | 1 |
| --- | --- | --- | --- |
| 42 | Motor FN100A | 15012406 | 1 |
| 43 | Motor Fixing Clip | 01722409 | 1 |
| 44 | Motor Clamp | 01702405 | 4 |
| 45 | Shaft Coupling | 73012403 | 2 |
| 46 | Mounting Board Sub-assy of Motor | 01332426 | 1 |
| 47 | Front Propeller Housing | 22202031 | 4 |
| 48 | Rear Propeller Housing | 22202032 | 4 |
| 49 | Rear Side Plate Assy | 01302419 | 1 |
| 50 | Motor Support Sub-assy | 01702410 | 1 |
| 51 | Filter | 11122012 | 2 |
| 52 | Gate Sub-assy | 01362401 | 1 |
| 53 | Front Grill | 22412011 | 2 |
| 54 | Front Grill Clasp 2 | 26252003 | 4 |
| 55 | Remote Controller Y512 （GREE） | 30512506 | 1 |
| 56 | Evaporator Assy | 01002405 | 1 |
| 57 | Front Grill Clasp 1 | 26252002 | 4 |
| 58 | Temp. Sensor | 390001215 | 1 |
| 59 | Sensor Insert B | 42020063 | 1 |
| 60 | Evaporator Cover | 01072417 | 1 |
| 61 | Left Decorative Plate | 26112032 | 1 |
| 62 | Left Mounting Plate | 01332405 | 1 |
| 63 | Left Side Plate Foam | 12312405 | 1 |
| 64 | Bearing Mounting Plate | 01332407 | 1 |
| 65 | Rear Side Plate of Air outlet | 01302405 | 1 |
| 66 | Swing Connecting Rod | 10582008 | 3 |
| 67 | Swing Connecting Rod | 10582009 | 2 |
| 68 | Swing Fan | 10512028 | 22 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | KFR-70D/NA1 | KF-70D/NA1 |  |
| 1 | Left Decorative Plate of Guide Plate Extruded Plastic Bar | 26112417 | 26112417 | 1 |
| 2 | Guide Louver I | 10512025 | 10512025 | 2 |
| 3 | Mounting Plate of Swing Louver | 01332410 | 01332410 | 1 |
| 4 | Guide Louver Holder | 24212020 | 24212020 | 3 |
| 5 | Guide Louver Support | 24222016 | 24222016 | 2 |
| 6 | Guide Louver | 10512404 | 10512404 | 1 |
| 7 | Guide Louver II | 10512026 | 10512026 | 2 |
| 8 | Right Decorative Plate of Guide Plate Extruded Plastic Bar | 26112421 | 26112421 | 1 |
| 9 | Mounting Plate (Left) of Swing Motor | 26152007 | 26152007 | 1 |
| 10 | Front Panel Sub-Assy | 01532414 | 01532414 | 1 |
| 11 | PCB Mounting Box | 20102138 | 20102138 | 1 |
| 12 | Display Board 6152BJ \6151BJ | 30546106 | 30546106 | 1 |
| 13 | Button Front Panel Sub-assy | 20162004 | 20162004 | 1 |
| 14 | Right Mounting Plate of Swing Motor | 26152008 | 26152008 | 1 |
| 15 | Stepping Motor (Air Guide) MP35CA | 15212402 | 15212402 | 2 |
| 16 | Swing Motor Clamp | 26112026 | 26112026 | 4 |
| 17 | Water Tray | 01272411 | 01272411 | 1 |
| 18 | Auxiliary Water Tray | 01272413 | 01272413 | 1 |
| 19 | Pipe Clip | 70812001 | 70812001 | 1 |
| 20 | Drainage Pipe Sub-assy | 05235433 | 05235433 | 1 |
| 21 | Handle | 26232001 | 26232001 | 4 |
| 22 | Right Side Plate Foam | 12312408 | 12312408 | 1 |
| 23 | Right Mounting Plate | 01332404 | 01332404 | 1 |
| 24 | Motor Bearing Block | 01792408 | 01792408 | 2 |
| 25 | Supporting Plate of Motor Support | 01792409 | 01792409 | 1 |
| 26 | Right Decorative Plate | 26112033 | 26112033 | 1 |
| 27 | Tube-exit Clamp of Evaporator | 01072424 | 01072424 | 1 |
| 28 | Electric Box Assy | 01403242 | 01403242 | 1 |
| 29 | Wire Seat | 24253001 | 24253001 | 1 |
| 30 | Wire-pressed Clamp | 24253002 | 24253002 | 1 |
| 31 | Terminal Board RS9413G | 42010178 | 42010178 | 1 |
| 32 | Fuse 5A 250VAC VDE | 46010013 | 46010013 | 1 |
| 33 | Mainboard 6152J\6152J | 30036052 | 30036051 | 1 |
| 34 | Ring of Bearing | 76512404 | 76512404 | 2 |
| 35 | Fan Bearing | 76512210 | 76512210 | 2 |
| 36 | Power Transformer SC28D | 43110194 | 43110194 | 1 |
| 37 | Electric Box Cover | 01413008 | 01413008 | 1 |
| 38 | Centrifugal Fan | 10312401 | 10312401 | 4 |
| 39 | Shaft Assy | 73012401 | 73012401 | 2 |
| 40 | Capacitor CBB61 3μF/450V | 33010027 | 33010027 | 1 |
| 41 | Capacitor Support | 01722408 | 01722408 | 1 |
| 42 | Motor FN100A | 15012406 | 15012406 | 1 |
| 43 | Motor Fixing Clip | 01722409 | 01722409 | 1 |

| 44 | Motor Clamp | 01702405 | 01702405 | 4 |
| --- | --- | --- | --- | --- |
| 45 | Shaft Coupling | 73012403 | 73012403 | 2 |
| 46 | Mounting Board Sub-assy of Motor | 01332426 | 01332426 | 1 |
| 47 | Front Propeller Housing | 22202031 | 22202031 | 4 |
| 48 | Rear Propeller Housing | 22202032 | 22202032 | 4 |
| 49 | Rear Side Plate Assy | 01302419 | 01302419 | 1 |
| 50 | Motor Support Sub-assy | 01702410 | 01702410 | 1 |
| 51 | Filter | 11122012 | 11122012 | 2 |
| 52 | Gate Sub-assy | 01362401 | 01362401 | 1 |
| 53 | Front Grill | 22412011 | 22412011 | 2 |
| 54 | Front Grill Clasp 2 | 26252003 | 26252003 | 4 |
| 55 | Remote Controller Y512 （GREE） | 30512506 | 30512506 | 1 |
| 56 | Evaporator Assy | 01002405 | 01002405 | 1 |
| 57 | Front Grill Clasp 1 | 26252002 | 26252002 | 4 |
| 58 | Temp. Sensor | 390001215 | 390001215 | 1 |
| 59 | Sensor Insert B | 42020063 | 42020063 | 1 |
| 60 | Evaporator Cover | 01072417 | 01072417 | 1 |
| 61 | Left Decorative Plate | 26112032 | 26112032 | 1 |
| 62 | Left Mounting Plate | 01332405 | 01332405 | 1 |
| 63 | Left Side Plate Foam | 12312405 | 12312405 | 1 |
| 64 | Bearing Mounting Plate | 01332407 | 01332407 | 1 |
| 65 | Rear Side Plate of Air outlet | 01302405 | 01302405 | 1 |
| 66 | Swing Connecting Rod | 10582008 | 10582008 | 3 |
| 67 | Swing Connecting Rod | 10582009 | 10582009 | 2 |
| 68 | Swing Fan | 10512028 | 10512028 | 22 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | GST24-22L/A(I) | GST24-22R/A(I) |  |
| 1 | Left Decorative Plate of Guide Plate Extruded Plastic Bar | 26112417 | 26112417 | 1 |
| 2 | Guide Louver I | 10512025 | 10512025 | 2 |
| 3 | Mounting Plate of Swing Louver | 01332410 | 01332410 | 1 |
| 4 | Guide Louver Holder | 24212020 | 24212020 | 3 |
| 5 | Guide Louver Support | 24222016 | 24222016 | 2 |
| 6 | Guide Louver | 10512404 | 10512404 | 1 |
| 7 | Guide Louver II | 10512026 | 10512026 | 2 |
| 8 | Right Decorative Plate of Guide Plate Extruded Plastic Bar | 26112421 | 26112421 | 1 |
| 9 | Mounting Plate (Left) of Swing Motor | 26152007 | 26152007 | 1 |
| 10 | Front Panel Sub-Assy | 01532414 | 01532414 | 1 |
| 11 | PCB Mounting Box | 20102138 | 20102138 | 1 |
| 12 | Display Board 6151AJ | 30546103 | 30546103 | 1 |
| 13 | Button Front Panel Sub-assy | 20162004 | 20162004 | 1 |
| 14 | Right Mounting Plate of Swing Motor | 26152008 | 26152008 | 1 |
| 15 | Stepping Motor (Air Guide) MP35CA | 15212402 | 15212402 | 2 |
| 16 | Swing Motor Clamp | 26112026 | 26112026 | 4 |
| 17 | Water Tray | 01272411 | 01272411 | 1 |
| 18 | Auxiliary Water Tray | 01272413 | 01272413 | 1 |
| 19 | Pipe Clip | 70812001 | 70812001 | 1 |
| 20 | Drainage Pipe Sub-assy | 05235433 | 05235433 | 1 |
| 21 | Handle | 26232001 | 26232001 | 4 |
| 22 | Right Side Plate Foam | 12312408 | 12312408 | 1 |
| 23 | Right Mounting Plate | 01332404 | 01332404 | 1 |
| 24 | Motor Bearing Block | 01792408 | 01792408 | 2 |
| 25 | Supporting Plate of Motor Support | 01792409 | 01792409 | 1 |
| 26 | Right Decorative Plate | 26112033 | 26112033 | 1 |
| 27 | Tube-exit Clamp of Evaporator | 01072424 | 01072424 | 1 |
| 28 | Electric Box Assy | 01403242 | 01403242 | 1 |
| 29 | Wire Seat | 24253001 | 24253001 | 1 |
| 30 | Wire-pressed Clamp | 24253002 | 24253002 | 1 |
| 31 | Terminal Board RS9413G | 42010178 | 42010178 | 1 |
| 32 | Fuse 5A 250VAC VDE | 46010013 | 46010013 | 1 |
| 33 | Mainboard 6151J | 30036051 | 30036052 | 1 |
| 34 | Ring of Bearing | 76512404 | 76512404 | 2 |
| 35 | Fan Bearing | 76512210 | 76512210 | 2 |
| 36 | Power Transformer SC28D | 43110194 | 43110194 | 1 |
| 37 | Electric Box Cover | 01413008 | 01413008 | 1 |
| 38 | Centrifugal Fan | 10312401 | 10312401 | 4 |
| 39 | Shaft Assy | 73012401 | 73012401 | 2 |
| 40 | Capacitor CBB61 3μF/450V | 33010027 | 33010027 | 1 |
| 41 | Capacitor Support | 01722408 | 01722408 | 1 |
| 42 | Motor FN100A | 15012406 | 15012406 | 1 |
| 43 | Motor Fixing Clip | 01722409 | 01722409 | 1 |

| 44 | Motor Clamp | 01702405 | 01702405 | 4 |
| --- | --- | --- | --- | --- |
| 45 | Shaft Coupling | 73012403 | 73012403 | 2 |
| 46 | Mounting Board Sub-assy of Motor | 01332426 | 01332426 | 1 |
| 47 | Front Propeller Housing | 22202031 | 22202031 | 4 |
| 48 | Rear Propeller Housing | 22202032 | 22202032 | 4 |
| 49 | Rear Side Plate Assy | 01302419 | 01302419 | 1 |
| 50 | Motor Support Sub-assy | 01702410 | 01702410 | 1 |
| 51 | Filter | 11122012 | 11122012 | 2 |
| 52 | Gate Sub-assy | 01362401 | 01362401 | 1 |
| 53 | Front Grill | 22412011 | 22412011 | 2 |
| 54 | Front Grill Clasp 2 | 26252003 | 26252003 | 4 |
| 55 | Remote Controller Y512 （GREE） | 30512506 | 30512506 | 1 |
| 56 | Evaporator Assy | 01002403 | 01002403 | 1 |
| 57 | Front Grill Clasp 1 | 26252002 | 26252002 | 4 |
| 58 | Temp. Sensor | 390001515 | 390001515 | 1 |
| 59 | Sensor Insert B | 42020063 | 42020063 | 1 |
| 60 | Evaporator Cover | 01072417 | 01072417 | 1 |
| 61 | Left Decorative Plate | 26112032 | 26112032 | 1 |
| 62 | Left Mounting Plate | 01332405 | 01332405 | 1 |
| 63 | Left Side Plate Foam | 12312405 | 12312405 | 1 |
| 64 | Bearing Mounting Plate | 01332407 | 01332407 | 1 |
| 65 | Rear Side Plate of Air outlet | 01302405 | 01302405 | 1 |
| 66 | Swing Connecting Rod | 10582008 | 10582008 | 3 |
| 67 | Swing Connecting Rod | 10582009 | 10582009 | 2 |
| 68 | Swing Fan | 10512028 | 10512028 | 22 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | KFR-120D/NA1-34005 | KF-120D/NA1-34005 |  |
| 1 | Left Decorative Plate of Guide Plate Extruded Plastic Bar | 26112415 | 26112415 | 1 |
| 2 | Guide Louver I | 10512025 | 10512025 | 2 |
| 3 | Mounting Plate of Swing Louver | 1332409 | 01332409 | 1 |
| 4 | Guide Louver Holder | 24212019 | 24212019 | 3 |
| 5 | Guide Louver Support | 24212018 | 24212018 | 2 |
| 6 | Guide Louver | 10512026 | 10512026 | 1 |
| 7 | Guide Louver II | 10512408 | 10512408 | 2 |
| 8 | Right Decorative Plate of Guide Plate Extruded Plastic Bar | 26112416 | 26112416 | 1 |
| 9 | Mounting Plate (Left) of Swing Motor | 26152005 | 26152005 | 1 |
| 10 | Front Panel Sub-Assy | 01532413 | 01532413 | 1 |
| 11 | PCB Mounting Box | 20102138 | 20102138 | 1 |
| 12 | Display Board 6152AJ \6151AJ | 30546103 | 30546103 | 1 |
| 13 | Button Front Panel Sub-assy | 201620041 | 201620041 | 1 |
| 14 | Right Mounting Plate of Swing Motor | 26152006 | 26152006 | 1 |
| 15 | Stepping Motor (Air Guide) MP35CA | 15212402 | 15212402 | 2 |
| 16 | Swing Motor Clamp | 26112026 | 26112026 | 4 |
| 17 | Water Tray | 01272408 | 01272408 | 1 |
| 18 | Auxiliary Water Tray | 01272409 | 01272409 | 1 |
| 19 | Pipe Clip | 70812001 | 70812001 | 1 |
| 20 | Drainage Pipe Sub-assy | 05235433 | 05235433 | 1 |
| 21 | Handle | 26232001 | 26232001 | 4 |
| 22 | Right Side Plate Foam | 12312402 | 12312402 | 1 |
| 23 | Right Mounting Plate | 01332404 | 01332404 | 1 |
| 24 | Motor Bearing Block | 01792408 | 01792408 | 2 |
| 25 | Supporting Plate of Motor Support | 01792407 | 01792407 | 1 |
| 26 | Right Decorative Plate | 26112027 | 26112027 | 1 |
| 27 | Tube-exit Clamp of Evaporator | 01072425 | 01072425 | 1 |
| 28 | Electric Box Assy | 01403242 | 01403242 | 1 |
| 29 | Wire Seat | 24253001 | 24253001 | 1 |
| 30 | Wire-pressed Clamp | 24253002 | 24253002 | 1 |
| 31 | Terminal Board RS9413G | 42010178 | 42010178 | 1 |
| 32 | Fuse 5A 250VAC VDE | 46010013 | 46010013 | 1 |
| 33 | Mainboard 6152J\6151J | 30036052 | 30036051 | 1 |
| 34 | Ring of Bearing | 76512404 | 76512404 | 2 |
| 35 | Fan Bearing | 76512210 | 76512210 | 2 |
| 36 | Power Transformer SC28D | 43110194 | 43110194 | 1 |
| 37 | Electric Box Cover | 1413008 | 1413008 | 1 |
| 38 | Centrifugal Fan | 10319051 | 10319051 | 4 |
| 39 | Shaft Assy | 73012402 | 73012402 | 2 |
| 40 | Capacitor CBB61 10μF/450V | 33010064 | 33010064 | 1 |
| 41 | Capacitor Support | 01722405 | 01722405 | 1 |
| 42 | Motor FN150A | 15012405 | 15012405 | 1 |
| 43 | Motor Fixing Clip | 01722410 | 01722410 | 1 |

| 44 | Motor Clamp | 01702405 | 01702405 | 4 |
| --- | --- | --- | --- | --- |
| 45 | Shaft Coupling | 73012403 | 73012403 | 2 |
| 46 | Mounting Board Sub-assy of Motor | 01332425 | 01332425 | 1 |
| 47 | Front Propeller Housing | 22202030 | 22202030 | 4 |
| 48 | Rear Propeller Housing | 22202029 | 22202029 | 4 |
| 49 | Rear Side Plate Assy | 01302411 | 01302411 | 1 |
| 50 | Motor Support Sub-assy | 01702411 | 01702411 | 1 |
| 51 | Filter | 11122013 | 11122013 | 2 |
| 52 | Gate Sub-assy | 01362407 | 01362407 | 1 |
| 53 | Front Grill | 22412010 | 22412010 | 2 |
| 54 | Front Grill Clasp 2 | 26252003 | 26252003 | 4 |
| 55 | Remote Controller Y512 （GREE） | 30512506 | 30512506 | 1 |
| 56 | Evaporator Assy | 01002406 | 01002406 | 1 |
| 57 | Front Grill Clasp 1 | 26252002 | 26252002 | 4 |
| 58 | Temp. Sensor | 390001215 | 390001215 | 1 |
| 59 | Sensor Insert B | 42020063 | 42020063 | 1 |
| 60 | Evaporator Cover | 01072409 | 01072409 | 1 |
| 61 | Left Decorative Plate | 26112028 | 26112028 | 1 |
| 62 | Left Mounting Plate | 01332405 | 01332405 | 1 |
| 63 | Left Side Plate Foam | 12312401 | 12312401 | 1 |
| 64 | Bearing Mounting Plate | 01332406 | 01332406 | 1 |
| 65 | Rear Side Plate of Air outlet | 01302416 | 01302416 | 1 |
| 66 | Swing Connecting Rod | 10582008 | 10582008 | 3 |
| 67 | Swing Connecting Rod | 10582009 | 10582009 | 2 |
| 68 | Swing Fan | 10512027 | 10512027 | 22 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | GST60-22L/A(I) | GST60-22R/A(I) |  |
| 1 | Left Decorative Plate of Guide Plate Extruded Plastic Bar | 26112415 | 26112415 | 1 |
| 2 | Guide Louver I | 10512025 | 10512025 | 2 |
| 3 | Mounting Plate of Swing Louver | 1332409 | 01332409 | 1 |
| 4 | Guide Louver Holder | 24212019 | 24212019 | 4 |
| 5 | Guide Louver Support | 24212018 | 24212018 | 3 |
| 6 | Guide Louver | 10512026 | 10512026 | 3 |
| 7 | Guide Louver II | 10512408 | 10512408 | 1 |
| 8 | Right Decorative Plate of Guide Plate Extruded Plastic Bar | 26112416 | 26112416 | 1 |
| 9 | Mounting Plate (Left) of Swing Motor | 26152005 | 26152005 | 1 |
| 10 | Front Panel Sub-Assy | 01532413 | 01532413 | 1 |
| 11 | PCB Mounting Box | 20102138 | 20102138 | 1 |
| 12 | Display Board 6151AJ | 30546103 | 30546103 | 1 |
| 13 | Button Front Panel Sub-assy | 201620041 | 201620041 | 1 |
| 14 | Right Mounting Plate of Swing Motor | 26152006 | 26152006 | 1 |
| 15 | Stepping Motor (Air Guide) MP35CA | 15212402 | 15212402 | 1 |
| 16 | Swing Motor Clamp | 26112026 | 26112026 | 2 |
| 17 | Water Tray | 01272407 | 01272407 | 1 |
| 18 | Auxiliary Water Tray | 0272409 | 01272409 | 1 |
| 19 | Pipe Clip | 70812001 | 70812001 | 1 |
| 20 | Drainage Pipe Sub-assy | 05235433 | 05235433 | 1 |
| 21 | Handle | 26232001 | 26232001 | 4 |
| 22 | Right Side Plate Foam | 12312402 | 12312402 | 1 |
| 23 | Right Mounting Plate | 13322402 | 01332404 | 1 |
| 24 | Motor Bearing Block | 01792408 | 01792408 | 2 |
| 25 | Supporting Plate of Motor Support | 01792407 | 01792407 | 1 |
| 26 | Right Decorative Plate | 26112027 | 26112027 | 1 |
| 27 | Tube-exit Clamp of Evaporator | 01072425 | 01072425 | 1 |
| 28 | Electric Box Assy | 01403242 | 01403242 | 1 |
| 29 | Wire Seat | 24253001 | 24253001 | 1 |
| 30 | Wire-pressed Clamp | 24253002 | 24253002 | 1 |
| 31 | Terminal Board RS9413G | 42011104 | 42011104 | 1 |
| 32 | Fuse 5A 250VAC VDE | 46010013 | 46010013 | 1 |
| 33 | Mainboard 6151J | 30036051 | 30036052 | 1 |
| 34 | Ring of Bearing | 76512404 | 76512404 | 2 |
| 35 | Fan Bearing | 76512210 | 76512210 | 2 |
| 36 | Power Transformer SC28D | 43110194 | 43110194 | 1 |
| 37 | Electric Box Cover | 01413008 | 01413008 | 1 |
| 38 | Centrifugal Fan | 10319051 | 10319051 | 4 |
| 39 | Shaft Assy | 73012402 | 73012402 | 2 |
| 40 | Capacitor CBB61 10μF/450V | 33010056 | 33010056 | 1 |
| 41 | Capacitor Support | 01711405 | 01722405 | 1 |
| 42 | Motor FN180A | 15012404 | 15012404 | 1 |
| 43 | Motor Fixing Clip | 01722410 | 01722410 | 1 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | GST60-22L/A(I) | GST60-22R/A(I) |  |
| 44 | Motor Clamp | 01702405 | 01702405 | 1 |
| 45 | Shaft Coupling | 73012403 | 73012403 | 2 |
| 46 | Mounting Board Sub-assy of Motor | 01332425 | 01332425 | 1 |
| 47 | Front Propeller Housing | 22202030 | 22202030 | 4 |
| 48 | Rear Propeller Housing | 22202029 | 22202029 | 4 |
| 49 | Rear Side Plate Assy | 01302411 | 01302411 | 1 |
| 50 | Motor Support Sub-assy | 01702411 | 01702411 | 1 |
| 51 | Filter | 11122013 | 11122013 | 1 |
| 52 | Gate Sub-assy | 01362407 | 01362407 | 1 |
| 53 | Front Grill | 22412010 | 22412010 | 4 |
| 54 | Front Grill Clasp 2 | 26252003 | 26252003 | 8 |
| 55 | Remote Controller Y512 （GREE） | 30512506 | 30512506 | 1 |
| 56 | Evaporator Assy | 01002401 | 01002401 | 1 |
| 57 | Front Grill Clasp 1 | 26252002 | 26252002 | 8 |
| 58 | Temp. Sensor | 390001515 | 390001215 | 1 |
| 59 | Sensor Insert B | 42020063 | 42020063 | 9 |
| 60 | Evaporator Cover | 01072409 | 01072409 | 1 |
| 61 | Left Decorative Plate | 26112028 | 26112028 | 1 |
| 62 | Left Mounting Plate | 01332405 | 01332405 | 1 |
| 63 | Left Side Plate Foam | 12312401 | 12312401 | 1 |
| 64 | Bearing Mounting Plate | 01332406 | 01332406 | 1 |
| 65 | Rear Side Plate of Air outlet | 01302416 | 01302416 | 1 |
| 66 | Swing Connecting Rod | 10582008 | 10582008 | 2 |
| 67 | Swing Connecting Rod | 10582009 | 10582009 | 4 |
| 68 | Swing Fan | 10512027 | 10512027 | 26 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | GST60-38R/A(I) | GST60-38L/A(I) |  |
| 1 | Left Decorative Plate of Guide Plate Extruded Plastic Bar | 26112415 | 26112415 | 1 |
| 2 | Guide Louver I | 10512025 | 10512025 | 2 |
| 3 | Mounting Plate of Swing Louver | 01332409 | 01332409 | 1 |
| 4 | Guide Louver Holder | 24212019 | 24212019 | 4 |
| 5 | Guide Louver Support | 24212018 | 24212018 | 3 |
| 6 | Guide Louver | 10512026 | 10512026 | 3 |
| 7 | Guide Louver II | 10512408 | 10512408 | 1 |
| 8 | Right Decorative Plate of Guide Plate Extruded Plastic Bar | 26112416 | 26112416 | 1 |
| 9 | Mounting Plate (Left) of Swing Motor | 26152005 | 26152005 | 1 |
| 10 | Front Panel Sub-Assy | 01532413 | 01532413 | 1 |
| 11 | PCB Mounting Box | 20102138 | 20102138 | 1 |
| 12 | Display Board 6152AJ | 30546104 | 30546104 | 1 |
| 13 | Button Front Panel Sub-assy | 201620041 | 201620041 | 1 |
| 14 | Right Mounting Plate of Swing Motor | 26152006 | 26152006 | 1 |
| 15 | Stepping Motor (Air Guide) MP35CA | 15212402 | 15212402 | 1 |
| 16 | Swing Motor Clamp | 26112026 | 26112026 | 2 |
| 17 | Water Tray | 01272407 | 01272407 | 1 |
| 18 | Auxiliary Water Tray | 01272409 | 01272409 | 1 |
| 19 | Pipe Clip | 70812001 | 70812001 | 1 |
| 20 | Drainage Pipe Sub-assy | 05235433 | 05235433 | 1 |
| 21 | Handle | 26232001 | 26232001 | 4 |
| 22 | Right Side Plate Foam | 12312402 | 12312402 | 1 |
| 23 | Right Mounting Plate | 01332404 | 01332404 | 1 |
| 24 | Motor Bearing Block | 01792408 | 01792408 | 2 |
| 25 | Supporting Plate of Motor Support | 01792407 | 01792407 | 1 |
| 26 | Right Decorative Plate | 26112027 | 26112027 | 1 |
| 27 | Tube-exit Clamp of Evaporator | 01072425 | 01072425 | 1 |
| 28 | Electric Box Assy | 01403242 | 01403242 | 1 |
| 29 | Wire Seat | 24253001 | 24253001 | 1 |
| 30 | Wire-pressed Clamp | 24253002 | 24253002 | 1 |
| 31 | Terminal Board RS9413G | 42010178 | 42010178 | 1 |
| 32 | Fuse 5A 250VAC VDE | 46010013 | 46010013 | 1 |
| 33 | Mainboard 6152J | 30036051 | 30036052 | 1 |
| 34 | Ring of Bearing | 76512404 | 76512404 | 2 |
| 35 | Fan Bearing | 76512210 | 76512210 | 2 |
| 36 | Power Transformer SC28D | 43110194 | 43110194 | 1 |
| 37 | Electric Box Cover | 01413008 | 01413008 | 1 |
| 38 | Centrifugal Fan | 10319051 | 10319051 | 4 |
| 39 | Shaft Assy | 73012402 | 73012402 | 2 |
| 40 | Capacitor CBB61 10μF/450V | 33010056 | 33010056 | 1 |
| 41 | Capacitor Support | 01711405 | 01722405 | 1 |
| 42 | Motor FN180A | 15012404 | 15012404 | 1 |
| 43 | Motor Fixing Clip | 01722410 | 01722410 | 1 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | GST60-38R/A(I) | GST60-38L/A(I) |  |
| 44 | Motor Clamp | 01702405 | 01702405 | 1 |
| 45 | Shaft Coupling | 73012403 | 73012403 | 2 |
| 46 | Mounting Board Sub-assy of Motor | 01332425 | 01332425 | 1 |
| 47 | Front Propeller Housing | 22202030 | 22202030 | 4 |
| 48 | Rear Propeller Housing | 22202029 | 22202029 | 4 |
| 49 | Rear Side Plate Assy | 01302411 | 01302411 | 1 |
| 50 | Motor Support Sub-assy | 01702411 | 01702411 | 1 |
| 51 | Filter | 11122013 | 11122013 | 1 |
| 52 | Gate Sub-assy | 01362407 | 01362407 | 1 |
| 53 | Front Grill | 22412010 | 22412010 | 4 |
| 54 | Front Grill Clasp 2 | 26252003 | 26252003 | 8 |
| 55 | Remote Controller Y512 （GREE） | 30512506 | 30512506 | 1 |
| 56 | Evaporator Assy | 01002401 | 01002401 | 1 |
| 57 | Front Grill Clasp 1 | 26252002 | 26252002 | 8 |
| 58 | Temp. Sensor | 390001215 | 390001215 | 1 |
| 59 | Sensor Insert B | 42020063 | 42020063 | 1 |
| 60 | Capillary | 81020196 | 81020196 | 9 |
| 61 | Evaporator Cover | 01072409 | 01072409 | 1 |
| 62 | Left Decorative Plate | 26112028 | 26112028 | 1 |
| 63 | Left Mounting Plate | 01332405 | 01332405 | 1 |
| 64 | Left Side Plate Foam | 12312401 | 12312401 | 1 |
| 65 | Bearing Mounting Plate | 01332406 | 01332406 | 1 |
| 66 | Rear Side Plate of Air outlet | 01302416 | 01302416 | 1 |
| 67 | Swing Connecting Rod | 10582008 | 10582008 | 2 |
| 68 | Swing Connecting Rod | 10582009 | 10582009 | 4 |
| 69 | Swing Fan | 10512027 | 10512027 | 26 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | GST42-38L/A(I) | GST42-38R/A(I) |  |
| 1 | Left Decorative Plate of Guide Plate Extruded Plastic Bar | 26112415 | 26112415 | 1 |
| 2 | Guide Louver I | 10512025 | 10512025 | 2 |
| 3 | Mounting Plate of Swing Louver | 01332409 | 01332409 | 1 |
| 4 | Guide Louver Holder | 24212019 | 24212019 | 4 |
| 5 | Guide Louver Support | 24212018 | 24212018 | 3 |
| 6 | Guide Louver | 10512026 | 10512026 | 3 |
| 7 | Guide Louver II | 10512408 | 10512408 | 1 |
| 8 | Right Decorative Plate of Guide Plate Extruded Plastic Bar | 26112416 | 26112416 | 1 |
| 9 | Mounting Plate (Left) of Swing Motor | 26152005 | 26152005 | 1 |
| 10 | Front Panel Sub-Assy | 01532413 | 01532413 | 1 |
| 11 | PCB Mounting Box | 20102138 | 20102138 | 1 |
| 12 | Display Board 6151AJ | 30546103 | 30546104 | 1 |
| 13 | Button Front Panel Sub-assy | 201620041 | 201620041 | 1 |
| 14 | Right Mounting Plate of Swing Motor | 26152006 | 26152006 | 1 |
| 15 | Stepping Motor (Air Guide) MP35CA | 15212402 | 15212402 | 1 |
| 16 | Swing Motor Clamp | 26112026 | 26112026 | 2 |
| 17 | Water Tray | 01272407 | 01272407 | 1 |
| 18 | Auxiliary Water Tray | 01272409 | 01272409 | 1 |
| 19 | Pipe Clip | 70812001 | 70812001 | 1 |
| 20 | Drainage Pipe Sub-assy | 05235433 | 05235433 | 1 |
| 21 | Handle | 26232001 | 26232001 | 4 |
| 22 | Right Side Plate Foam | 12312402 | 12312402 | 1 |
| 23 | Right Mounting Plate | 01332404 | 01332404 | 1 |
| 24 | Motor Bearing Block | 01792408 | 01792408 | 2 |
| 25 | Supporting Plate of Motor Support | 01792407 | 01792407 | 1 |
| 26 | Right Decorative Plate | 26112027 | 26112027 | 1 |
| 27 | Tube-exit Clamp of Evaporator | 01072425 | 01072425 | 1 |
| 28 | Electric Box Assy | 01403242 | 01403242 | 1 |
| 29 | Wire Seat | 24253001 | 24253001 | 1 |
| 30 | Wire-pressed Clamp | 24253002 | 24253002 | 1 |
| 31 | Terminal Board RS9413G | 42010178 | 42010178 | 1 |
| 32 | Fuse 5A 250VAC VDE | 46010013 | 46010013 | 1 |
| 33 | Mainboard 6151J | 30036051 | 30036052 | 1 |
| 34 | Ring of Bearing | 76512404 | 76512404 | 2 |
| 35 | Fan Bearing | 76512210 | 76512210 | 2 |
| 36 | Power Transformer SC28D | 43110194 | 43110194 | 1 |
| 37 | Electric Box Cover | 01413008 | 01413008 | 1 |
| 38 | Centrifugal Fan | 10319051 | 10319051 | 4 |
| 39 | Shaft Assy | 73012402 | 73012402 | 2 |
| 40 | Capacitor CBB61 4μF/450V | 33010056 | 33010056 | 1 |
| 41 | Capacitor Support | 01711405 | 01722405 | 1 |
| 42 | Motor FN150A | 15012405 | 15012405 | 1 |
| 43 | Motor Fixing Clip | 01722410 | 01722410 | 1 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | GST42-38L/A(I) | GST42-38R/A(I) |  |
| 44 | Motor Clamp | 01702405 | 01702405 | 1 |
| 45 | Shaft Coupling | 73012403 | 73012403 | 2 |
| 46 | Mounting Board Sub-assy of Motor | 01332425 | 01332425 | 1 |
| 47 | Front Propeller Housing | 22202030 | 22202030 | 4 |
| 48 | Rear Propeller Housing | 22202029 | 22202029 | 4 |
| 49 | Rear Side Plate Assy | 01302411 | 01302411 | 1 |
| 50 | Motor Support Sub-assy | 01702411 | 01702411 | 1 |
| 51 | Filter | 11122013 | 11122013 | 1 |
| 52 | Gate Sub-assy | 01362407 | 01362407 | 1 |
| 53 | Front Grill | 22412010 | 22412010 | 4 |
| 54 | Front Grill Clasp 2 | 26252003 | 26252003 | 8 |
| 55 | Remote Controller Y512 （GREE） | 30512506 | 30512506 | 1 |
| 56 | Evaporator Assy | 01002401 | 01002401 | 1 |
| 57 | Front Grill Clasp 1 | 26252002 | 26252002 | 8 |
| 58 | Temp. Sensor | 390001215 | 390001215 | 1 |
| 59 | Sensor Insert B | 42020063 | 42020063 | 1 |
| 60 | Capillary | 81020196 | 81020196 | 9 |
| 61 | Evaporator Cover | 01072409 | 01072409 | 1 |
| 62 | Left Decorative Plate | 26112028 | 26112028 | 1 |
| 63 | Left Mounting Plate | 01332405 | 01332405 | 1 |
| 64 | Left Side Plate Foam | 12312401 | 12312401 | 1 |
| 65 | Bearing Mounting Plate | 01332406 | 01332406 | 1 |
| 66 | Rear Side Plate of Air outlet | 01302416 | 01302416 | 1 |
| 67 | Swing Connecting Rod | 10582008 | 10582008 | 2 |
| 68 | Swing Connecting Rod | 10582009 | 10582009 | 4 |
| 69 | Swing Fan | 10512027 | 10512027 | 26 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | GST42-38L/A(I) | GST42-38R/A(I) |  |
| 1 | Left Decorative Plate of Guide Plate Extruded Plastic Bar | 26112415 | 26112415 | 1 |
| 2 | Guide Louver I | 10512025 | 10512025 | 2 |
| 3 | Mounting Plate of Swing Louver | 01332409 | 01332409 | 1 |
| 4 | Guide Louver Holder | 24212019 | 24212019 | 4 |
| 5 | Guide Louver Support | 24212018 | 24212018 | 3 |
| 6 | Guide Louver | 10512026 | 10512026 | 3 |
| 7 | Guide Louver II | 10512408 | 10512408 | 1 |
| 8 | Right Decorative Plate of Guide Plate Extruded Plastic Bar | 26112416 | 26112416 | 1 |
| 9 | Mounting Plate (Left) of Swing Motor | 26152005 | 26152005 | 1 |
| 10 | Front Panel Sub-Assy | 01532413 | 01532413 | 1 |
| 11 | PCB Mounting Box | 20102138 | 20102138 | 1 |
| 12 | Display Board 6151AJ | 30546103 | 30546104 | 1 |
| 13 | Button Front Panel Sub-assy | 201620041 | 201620041 | 1 |
| 14 | Right Mounting Plate of Swing Motor | 26152006 | 26152006 | 1 |
| 15 | Stepping Motor (Air Guide) MP35CA | 15212402 | 15212402 | 1 |
| 16 | Swing Motor Clamp | 26112026 | 26112026 | 2 |
| 17 | Water Tray | 01272407 | 01272407 | 1 |
| 18 | Auxiliary Water Tray | 01272409 | 01272409 | 1 |
| 19 | Pipe Clip | 70812001 | 70812001 | 1 |
| 20 | Drainage Pipe Sub-assy | 05235433 | 05235433 | 1 |
| 21 | Handle | 26232001 | 26232001 | 4 |
| 22 | Right Side Plate Foam | 12312402 | 12312402 | 1 |
| 23 | Right Mounting Plate | 01332404 | 01332404 | 1 |
| 24 | Motor Bearing Block | 01792408 | 01792408 | 2 |
| 25 | Supporting Plate of Motor Support | 01792407 | 01792407 | 1 |
| 26 | Right Decorative Plate | 26112027 | 26112027 | 1 |
| 27 | Tube-exit Clamp of Evaporator | 01072425 | 01072425 | 1 |
| 28 | Electric Box Assy | 01403242 | 01403242 | 1 |
| 29 | Wire Seat | 24253001 | 24253001 | 1 |
| 30 | Wire-pressed Clamp | 24253002 | 24253002 | 1 |
| 31 | Terminal Board RS9413 | 42011104 | 42011104 | 1 |
| 32 | Fuse 5A 250VAC VDE | 46010013 | 46010013 | 1 |
| 33 | Mainboard 6151J | 30036051 | 30036052 | 1 |
| 34 | Ring of Bearing | 76512404 | 76512404 | 2 |
| 35 | Fan Bearing | 76512210 | 76512210 | 2 |
| 36 | Power Transformer SC28D | 43110194 | 43110194 | 1 |
| 37 | Electric Box Cover | 01413008 | 01413008 | 1 |
| 38 | Centrifugal Fan | 10319051 | 10319051 | 4 |
| 39 | Shaft Assy | 73012402 | 73012402 | 2 |
| 40 | Capacitor CBB61 4μF/450V | 33010011 | 33010011 | 1 |
| 41 | Capacitor Support | 01711405 | 01722405 | 1 |
| 42 | Motor FN150A | 15012405 | 15012405 | 1 |
| 43 | Motor Fixing Clip | 01722410 | 01722410 | 1 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | GST42-22L/A(I) | GST42-22R/A(I) |  |
| 44 | Motor Clamp | 01702405 | 01702405 | 1 |
| 45 | Shaft Coupling | 73012403 | 73012403 | 2 |
| 46 | Mounting Board Sub-assy of Motor | 01332425 | 01332425 | 1 |
| 47 | Front Propeller Housing | 22202030 | 22202030 | 4 |
| 48 | Rear Propeller Housing | 22202029 | 22202029 | 4 |
| 49 | Rear Side Plate Assy | 01302411 | 01302411 | 1 |
| 50 | Motor Support Sub-assy | 01702411 | 01702411 | 1 |
| 51 | Filter | 11122013 | 11122013 | 1 |
| 52 | Gate Sub-assy | 01362407 | 01362407 | 1 |
| 53 | Front Grill | 22412010 | 22412010 | 4 |
| 54 | Front Grill Clasp 2 | 26252003 | 26252003 | 8 |
| 55 | Remote Controller Y512 （GREE） | 30512506 | 30512506 | 1 |
| 56 | Evaporator Assy | 01002401 | 01002401 | 1 |
| 57 | Front Grill Clasp 1 | 26252002 | 26252002 | 8 |
| 58 | Temp. Sensor | 390001215 | 390001215 | 1 |
| 59 | Sensor Insert B | 42020063 | 42020063 | 1 |
| 60 | Capillary | 81020196 | 81020196 | 9 |
| 61 | Evaporator Cover | 01072409 | 01072409 | 1 |
| 62 | Left Decorative Plate | 26112028 | 26112028 | 1 |
| 63 | Left Mounting Plate | 01332405 | 01332405 | 1 |
| 64 | Left Side Plate Foam | 12312401 | 12312401 | 1 |
| 65 | Bearing Mounting Plate | 01332406 | 01332406 | 1 |
| 66 | Rear Side Plate of Air outlet | 01302416 | 01302416 | 1 |
| 67 | Swing Connecting Rod | 10582008 | 10582008 | 2 |
| 68 | Swing Connecting Rod | 10582009 | 10582009 | 4 |
| 69 | Swing Fan | 10512027 | 10512027 | 26 |

Exploded View of Components and Parts of Indoor Unit

| Components and Parts List of Indoor Unit |
| --- |
| No. | Description | Part Code | Qty |
|  |  | GST36-22L/A(I) | GST36-22R/A(I) |  |
| 1 | Left Decorative Plate of Guide Plate Extruded Plastic Bar | 26112415 | 26112415 | 1 |
| 2 | Guide Louver I | 10512025 | 10512025 | 2 |
| 3 | Mounting Plate of Swing Louver | 01332409 | 01332409 | 1 |
| 4 | Guide Louver Holder | 24212019 | 24212019 | 4 |
| 5 | Guide Louver Support | 24222018 | 24222018 | 3 |
| 6 | Guide Louver II | 10512026 | 10512026 | 3 |
| 7 | Guide Louver | 10512408 | 10512408 | 1 |
| 8 | Right Decorative Plate of Guide Plate Extruded Plastic Bar | 26112416 | 26112416 | 1 |
| 9 | Mounting Plate (Left) of Swing Motor | 26152005 | 26152005 | 1 |
| 10 | Front Panel Sub-Assy | 01532413 | 01532413 | 1 |
| 11 | PCB Mounting Box | 20102138 | 20102138 | 1 |
| 12 | Display Board 6152J | 30292703 | 30292703 | 1 |
| 13 | Button Front Panel Sub-assy | 201620041 | 201620041 | 1 |
| 14 | Right Mounting Plate of Swing Motor | 26152006 | 26152006 | 1 |
| 15 | Stepping Motor (Air Guide) MP35CA | 15212402 | 15212402 | 1 |
| 16 | Swing Motor Clamp | 26112026 | 26112026 | 2 |
| 17 | Water Tray | 01272408 | 01272408 | 1 |
| 18 | Pipe Clip | 70812001 | 70812001 | 1 |
| 19 | Drainage Pipe Sub-assy | 05235433 | 05235433 | 1 |
| 20 | Handle | 26232001 | 26232001 | 4 |
| 21 | Right Side Plate Foam | 12312402 | 12312402 | 1 |
| 22 | Right Mounting Plate | 01332404 | 01332404 | 1 |
| 23 | Motor Bearing Block | 01792408 | 01792408 | 2 |
| 24 | Supporting Plate of Motor Support | 01792407 | 01792407 | 2 |
| 25 | Right Decorative Plate | 26112027 | 26112027 | 1 |
| 26 | Tube-exit Clamp of Evaporator | 01072425 | 01072425 | 1 |
| 27 | Electric Box Assy | 01403242 | 01403242 | 1 |
| 28 | Wire Seat | 24253001 | 24253001 | 1 |
| 29 | Wire-pressed Clamp | 24253002 | 24253002 | 1 |
| 30 | Terminal Board RS9413G | 42010178 | 42010178 | 1 |
| 31 | Fuse 5A 250VAC VDE | 46010013 | 46010013 | 1 |
| 32 | Mainboard 6152J | 30036051 | 30036051 | 1 |
| 33 | Ring of Bearing | 76512404 | 76512404 | 2 |
| 34 | Fan Bearing | 76512210 | 76512210 | 2 |
| 35 | Power Transformer SC28D | 43110194 | 43110194 | 1 |
| 36 | Electric Box Cover | 1413008 | 1413008 | 1 |
| 37 | Centrifugal Fan | 10319051 | 10319051 | 4 |
| 38 | Shaft Assy | 73012402 | 73012402 | 2 |
| 39 | 4μF/450V(TUV/VDE) | 33010011 | 33010011 | 1 |
| 40 | Capacitor Support | 01722405 | 01722405 | 1 |

| 41 | Motor FN150A | 15012405 | 15012405 | 1 |
| --- | --- | --- | --- | --- |
| 42 | Motor Fixing Clip | 01722410 | 01722410 | 1 |
| 43 | Motor Clamp | 01702405 | 01702405 | 1 |
| 44 | Shaft Coupling | 73012403 | 73012403 | 2 |
| 45 | Mounting Board Sub-assy of Motor | 01332425 | 01332425 | 1 |
| 46 | Front Propeller Housing | 22202030 | 22202030 | 4 |
| 47 | Rear Propeller Housing | 22202029 | 22202029 | 4 |
| 48 | Rear Side Plate Assy | 01302411 | 01302411 | 1 |
| 49 | Motor Support Sub-assy | 01702411 | 01702411 | 1 |
| 50 | Filter | 11122013 | 11122013 | 1 |
| 51 | Gate Sub-assy | 01362407 | 01362407 | 1 |
| 52 | Front Grill | 22412010 | 22412010 | 1 |
| 53 | Front Grill Clasp 2 | 26252003 | 26252003 | 2 |
| 54 | Remote Controller Y512 （GREE） | 30512506 | 30512506 | 1 |
| 55 | Evaporator Assy | 01002408 | 01002408 | 1 |
| 56 | Front Grill Clasp 1 | 26252002 | 26252002 | 2 |
| 57 | Temp. Sensor | 390001215 | 390001215 | 1 |
| 58 | Sensor Insert B | 42020063 | 42020063 | 1 |
| 59 | Main Capillary | 81022105 | 81022105 | 4 |
| 60 | Evaporator Cover | 01072409 | 01072409 | 1 |
| 61 | Left Decorative Plate | 26112028 | 26112028 | 1 |
| 62 | Left Mounting Plate | 01332405 | 01332405 | 1 |
| 63 | Left Side Plate Foam | 12312401 | 12312401 | 1 |
| 64 | Bearing Mounting Plate | 01332406 | 01332406 | 1 |
| 65 | Rear Side Plate of Air outlet | 01302416 | 01302416 | 1 |
| 66 | Swing Connecting Rod | 10582008 | 10582008 | 2 |
| 67 | Swing Connecting Rod | 10512009 | 10512009 | 4 |
| 68 | Swing Fan | 10512027 | 10512027 | 26 |

Components and Parts List of Indoor Unit

| Components and Parts List of Indoor Unit |
| --- |
| No. | Description | Part Code | Qty |
|  |  | GST36-38L/A(I) | GST36-38R/A(I) |  |
| 1 | Left Decorative Plate of Guide Plate Extruded Plastic Bar | 26112415 | 26112415 | 1 |
| 2 | Guide Louver I | 10512025 | 10512025 | 2 |
| 3 | Mounting Plate of Swing Louver | 01332409 | 01332409 | 1 |
| 4 | Guide Louver Holder | 24212019 | 24212019 | 4 |
| 5 | Guide Louver Support | 24222018 | 24222018 | 3 |
| 6 | Guide Louver II | 10512026 | 10512026 | 3 |
| 7 | Guide Louver | 10512408 | 10512408 | 1 |
| 8 | Right Decorative Plate of Guide Plate Extruded Plastic Bar | 26112416 | 26112416 | 1 |
| 9 | Mounting Plate (Left) of Swing Motor | 26152005 | 26152005 | 1 |
| 10 | Front Panel Sub-Assy | 01532413 | 01532413 | 1 |
| 11 | PCB Mounting Box | 20102138 | 20102138 | 1 |
| 12 | Display Board 6152J | 30546103 | 30546104 | 1 |
| 13 | Button Front Panel Sub-assy | 201620041 | 201620041 | 1 |
| 14 | Right Mounting Plate of Swing Motor | 26152006 | 26152006 | 1 |
| 15 | Stepping Motor (Air Guide) MP35CA | 15212402 | 15212402 | 1 |
| 16 | Swing Motor Clamp | 26112026 | 26112026 | 2 |
| 17 | Water Tray | 01272408 | 01272408 | 1 |
| 18 | Pipe Clip | 70812001 | 70812001 | 1 |
| 19 | Drainage Pipe Sub-assy | 05235433 | 05235433 | 1 |
| 20 | Handle | 26232001 | 26232001 | 4 |
| 21 | Right Side Plate Foam | 12312402 | 12312402 | 1 |
| 22 | Right Mounting Plate | 01332404 | 01332404 | 1 |
| 23 | Motor Bearing Block | 01792408 | 01792408 | 2 |
| 24 | Supporting Plate of Motor Support | 01792407 | 01792407 | 2 |
| 25 | Right Decorative Plate | 26112027 | 26112027 | 1 |
| 26 | Tube-exit Clamp of Evaporator | 01072425 | 01072425 | 1 |
| 27 | Electric Box Assy | 01403242 | 01403242 | 1 |
| 28 | Wire Seat | 24253001 | 24253001 | 1 |
| 29 | Wire-pressed Clamp | 24253002 | 24253002 | 1 |
| 30 | Terminal Board RS9413G | 42010178 | 42010178 | 1 |
| 31 | Fuse 5A 250VAC VDE | 46010013 | 46010013 | 1 |
| 32 | Mainboard 6151J | 30036051 | 30036051 | 1 |
| 33 | Ring of Bearing | 76512404 | 76512404 | 2 |
| 34 | Fan Bearing | 76512210 | 76512210 | 2 |
| 35 | Power Transformer SC28D | 43110194 | 43110194 | 1 |
| 36 | Electric Box Cover | 1413008 | 1413008 | 1 |
| 37 | Centrifugal Fan | 10319051 | 10319051 | 4 |
| 38 | Shaft Assy | 73012402 | 73012402 | 2 |
| 39 | 4.5μF/450V(TUV/VDE) | 33010012 | 33010012 | 1 |
| 40 | Capacitor Support | 01722405 | 01722405 | 1 |

| 41 | Motor FN150A | 15012405 | 15012405 | 1 |
| --- | --- | --- | --- | --- |
| 42 | Motor Fixing Clip | 01722410 | 01722410 | 1 |
| 43 | Motor Clamp | 01702405 | 01702405 | 1 |
| 44 | Shaft Coupling | 73012403 | 73012403 | 2 |
| 45 | Mounting Board Sub-assy of Motor | 01332425 | 01332425 | 1 |
| 46 | Front Propeller Housing | 22202030 | 22202030 | 4 |
| 47 | Rear Propeller Housing | 22202029 | 22202029 | 4 |
| 48 | Rear Side Plate Assy | 01302411 | 01302411 | 1 |
| 49 | Motor Support Sub-assy | 01702411 | 01702411 | 1 |
| 50 | Filter | 11122013 | 11122013 | 1 |
| 51 | Gate Sub-assy | 01362407 | 01362407 | 1 |
| 52 | Front Grill | 22412010 | 22412010 | 1 |
| 53 | Front Grill Clasp 2 | 26252003 | 26252003 | 2 |
| 54 | Remote Controller Y512 （GREE） | 30512506 | 30512506 | 1 |
| 55 | Evaporator Assy | 01002407 | 01002407 | 1 |
| 56 | Front Grill Clasp 1 | 26252002 | 26252002 | 2 |
| 57 | Temp. Sensor | 390001215 | 390001215 | 1 |
| 58 | Sensor Insert B | 42020063 | 42020063 | 1 |
| 59 | Main Capillary | 03013447 | 03013447 | 4 |
| 60 | Evaporator Cover | 01072409 | 01072409 | 1 |
| 61 | Left Decorative Plate | 26112028 | 26112028 | 1 |
| 62 | Left Mounting Plate | 01332405 | 01332405 | 1 |
| 63 | Left Side Plate Foam | 12312401 | 12312401 | 1 |
| 64 | Bearing Mounting Plate | 01332406 | 01332406 | 1 |
| 65 | Rear Side Plate of Air outlet | 01302416 | 01302416 | 1 |
| 66 | Swing Connecting Rod | 10582008 | 10582008 | 2 |
| 67 | Swing Connecting Rod | 10512009 | 10512009 | 4 |
| 68 | Swing Fan | 10512027 | 10512027 | 26 |

Components and Parts List of Indoor Unit

| Components and Parts List of Indoor Unit |
| --- |
| No. | Description | Part Code | Qty |
|  |  | KFR-100D/B1-G | KFR-120D/B1-G |  |
| 1 | Left Decorative Plate of Guide Plate Extruded Plastic Bar | 26112415 | 26112415 | 1 |
| 2 | Guide Louver I | 10512025 | 10512025 | 2 |
| 3 | Mounting Plate of Swing Louver | 01332409 | 01332409 | 1 |
| 4 | Guide Louver Holder | 24212019 | 24212019 | 4 |
| 5 | Guide Louver Support | 24222018 | 24222018 | 3 |
| 6 | Guide Louver II | 10512026 | 10512026 | 3 |
| 7 | Guide Louver | 10512408 | 10512408 | 1 |
| 8 | Right Decorative Plate of Guide Plate Extruded Plastic Bar | 26112416 | 26112416 | 1 |
| 9 | Mounting Plate (Left) of Swing Motor | 26152005 | 26152005 | 1 |
| 10 | Front Panel Sub-Assy | 01532413 | 01532413 | 1 |
| 11 | PCB Mounting Box | 20102138 | 20102138 | 1 |
| 12 | Display Board 6152AJ | 30546103 | 30546104 | 1 |
| 13 | Button Front Panel Sub-assy | 201620041 | 201620041 | 1 |
| 14 | Right Mounting Plate of Swing Motor | 26152006 | 26152006 | 1 |
| 15 | Stepping Motor (Air Guide) MP35CA | 15212402 | 15212402 | 1 |
| 16 | Swing Motor Clamp | 26112026 | 26112026 | 2 |
| 17 | Water Tray | 01272408 | 01272407 | 1 |
| 18 | Auxiliary Water Tray | / | 01272409 | 1 |
| 19 | Pipe Clip | 70812001 | 70812001 | 1 |
| 20 | Drainage Pipe Sub-assy | 05235433 | 05235433 | 1 |
| 21 | Handle | 26232001 | 26232001 | 4 |
| 22 | Right Side Plate Foam | 12312402 | 12312402 | 1 |
| 23 | Right Mounting Plate | 01332404 | 01332404 | 1 |
| 24 | Motor Bearing Block | 01792408 | 01792408 | 2 |
| 25 | Supporting Plate of Motor Support | 01792407 | 01792407 | 1 |
| 26 | Right Decorative Plate | 26112027 | 26112027 | 1 |
| 27 | Tube-exit Clamp of Evaporator | 01072425 | 01072425 | 1 |
| 28 | Electric Box Assy | 01403242 | 01403242 | 1 |
| 29 | Wire Seat | 24253001 | 24253001 | 1 |
| 30 | Wire-pressed Clamp | 24253002 | 24253002 | 1 |
| 31 | Terminal Board RS9413G | 42010178 | 42010178 | 1 |
| 32 | Fuse 5A 250VAC VDE | 46010013 | 46010013 | 1 |
| 33 | Mainboard 6152J | 30036052 | 30036052 | 1 |
| 34 | Ring of Bearing | 76512404 | 76512404 | 2 |
| 35 | Fan Bearing | 76512210 | 76512210 | 2 |
| 36 | Power Transformer SC28D | 43110194 | 43110194 | 1 |
| 37 | Electric Box Cover | 1413008 | 1413008 | 1 |
| 38 | Centrifugal Fan | 10319051 | 10319051 | 4 |
| 39 | Shaft Assy | 73012402 | 73012402 | 2 |
| 40 | Capacitor CBB61 | 33010012 | 33010012 | 1 |

| 41 | Capacitor Support | 01722405 | 01722405 | 1 |
| --- | --- | --- | --- | --- |
| 42 | Motor FN100A | 15012405 | 15012405 | 1 |
| 43 | Motor Fixing Clip | 01722410 | 01722410 | 1 |
| 44 | Motor Clamp | 01702405 | 01702405 | 1 |
| 45 | Shaft Coupling | 73012403 | 73012403 | 2 |
| 46 | Mounting Board Sub-assy of Motor | 01332425 | 01332425 | 1 |
| 47 | Front Propeller Housing | 22202030 | 22202030 | 4 |
| 48 | Rear Propeller Housing | 22202029 | 22202029 | 4 |
| 49 | Rear Side Plate Assy | 01302411 | 01302411 | 1 |
| 50 | Motor Support Sub-assy | 01702411 | 01702411 | 1 |
| 51 | Filter | 11122013 | 11122013 | 1 |
| 52 | Gate Sub-assy | 01362407 | 01362407 | 1 |
| 53 | Front Grill | 22412010 | 22412010 | 4 |
| 54 | Front Grill Clasp 2 | 26252003 | 26252003 | 8 |
| 55 | Remote Controller Y512 （GREE） | 30512506 | 30512506 | 1 |
| 56 | Evaporator Assy | 010324061 | 01002401 | 1 |
| 57 | Front Grill Clasp 1 | 26252002 | 26252002 | 8 |
| 58 | Temp. Sensor(20K) | 390001215 | 390001215 | 1 |
| 59 | Sensor Insert B | 42020063 | 42020063 | 1 |
| 60 | Capillary | 81020137 | 81020196 | 1 |
| 61 | Evaporator Cover | 01072409 | 01072409 | 1 |
| 62 | Left Decorative Plate | 26112028 | 26112028 | 1 |
| 63 | Left Mounting Plate | 01332405 | 01332405 | 1 |
| 64 | Left Side Plate Foam | 12312401 | 12312401 | 1 |
| 65 | Bearing Mounting Plate | 01332406 | 01332406 | 1 |
| 66 | Rear Side Plate of Air outlet | 01302416 | 01302416 | 1 |
| 67 | Swing Connecting Rod | 10582008 | 10582008 | 2 |
| 68 | Swing Connecting Rod | 10512009 | 10512009 | 4 |
| 69 | Swing Fan | 10512027 | 10512027 | 26 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | KF-100D/NA1-34005 | KFR-100D/NA1-34005 |  |
| 1 | Left Decorative Plate of Guide Plate Extruded Plastic Bar | 26112415 | 26112415 | 1 |
| 2 | Guide Louver I | 10512025 | 10512025 | 2 |
| 3 | Mounting Plate of Swing Louver | 01332409 | 01332409 | 1 |
| 4 | Guide Louver Holder | 24212019 | 24212019 | 4 |
| 5 | Guide Louver Support | 24212018 | 24212018 | 3 |
| 6 | Guide Louver | 10512026 | 10512026 | 3 |
| 7 | Guide Louver II | 10512408 | 10512408 | 1 |
| 8 | Right Decorative Plate of Guide Plate Extruded Plastic Bar | 26112416 | 26112416 | 1 |
| 9 | Mounting Plate (Left) of Swing Motor | 26152005 | 26152005 | 1 |
| 10 | Front Panel Sub-Assy | 01532413 | 01532413 | 1 |
| 11 | PCB Mounting Box | 20102138 | 20102138 | 1 |
| 12 | Display Board 6151AJ\6152AJ | 30546103 | 30546104 | 1 |
| 13 | Button Front Panel Sub-assy | 201620041 | 201620041 | 1 |
| 14 | Right Mounting Plate of Swing Motor | 26152006 | 26152006 | 1 |
| 15 | Stepping Motor (Air Guide) MP35CA | 15212402 | 15212402 | 1 |
| 16 | Swing Motor Clamp | 26112026 | 26112026 | 2 |
| 17 | Water Tray Assy | 01272408 | 01272407 | 1 |
| 19 | Pipe Clip | 70812001 | 70812001 | 1 |
| 20 | Drainage Pipe Sub-assy | 05235433 | 05235433 | 1 |
| 21 | Handle | 26232001 | 26232001 | 4 |
| 22 | Right Side Plate Foam | 12312402 | 12312402 | 1 |
| 23 | Right Mounting Plate | 01332404 | 01332404 | 1 |
| 24 | Motor Bearing Block | 01792408 | 01792408 | 2 |
| 25 | Supporting Plate of Motor Support | 01792407 | 01792407 | 1 |
| 26 | Right Decorative Plate | 26112027 | 26112027 | 1 |
| 27 | Tube-exit Clamp of Evaporator | 01072425 | 01072425 | 1 |
| 28 | Electric Box Assy | 01403242 | 01403242 | 1 |
| 29 | Wire Seat | 24253001 | 24253001 | 1 |
| 30 | Wire-pressed Clamp | 24253002 | 24253002 | 1 |
| 31 | Terminal Board RS9413G | 42010178 | 42010178 | 1 |
| 32 | Fuse 5A 250VAC VDE | 46010013 | 46010013 | 1 |
| 33 | Mainboard 6151J\6152J | 30036051 | 30036052 | 1 |
| 34 | Ring of Bearing | 76512404 | 76512404 | 2 |
| 35 | Fan Bearing | 76512210 | 76512210 | 2 |
| 36 | Power Transformer SC28D | 43110194 | 43110194 | 1 |
| 37 | Electric Box Cover | 01413008 | 01413008 | 1 |
| 38 | Centrifugal Fan | 10319051 | 10319051 | 4 |
| 39 | Shaft Assy | 73012402 | 73012402 | 2 |
| 40 | Capacitor | 33010012 | 33010012 | 1 |
| 41 | Capacitor Support | 01722405 | 01722405 | 1 |
| 42 | Motor FN150A | 15012405 | 15012405 | 1 |
| 43 | Motor Fixing Clip | 01722410 | 01722410 | 1 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | KF-100D/NA1-34005 | KFR-100D/NA1-34005 |  |
| 44 | Motor Clamp | 01702405 | 01702405 | 1 |
| 45 | Shaft Coupling | 73012403 | 73012403 | 2 |
| 46 | Mounting Board Sub-assy of Motor | 01332425 | 01332425 | 1 |
| 47 | Front Propeller Housing | 22202030 | 22202030 | 4 |
| 48 | Rear Propeller Housing | 22202029 | 22202029 | 4 |
| 49 | Rear Side Plate Assy | 01302411 | 01302411 | 1 |
| 50 | Motor Support Sub-assy | 01702411 | 01702411 | 1 |
| 51 | Filter | 11122013 | 11122013 | 1 |
| 52 | Gate Sub-assy | 01362407 | 01362407 | 1 |
| 53 | Front Grill | 22412010 | 22412010 | 4 |
| 54 | Front Grill Clasp 2 | 26252003 | 26252003 | 8 |
| 55 | Remote Controller Y512 （GREE） | 30512506 | 30512506 | 1 |
| 56 | Evaporator Assy | 01002406 | 01002406 | 1 |
| 57 | Front Grill Clasp 1 | 26252002 | 26252002 | 8 |
| 58 | Temp. Sensor | 390001215 | 390001215 | 1 |
| 59 | Sensor Insert B | 42020063 | 42020063 | 1 |
| 60 | Main Capillary | 03012401 | 03012401 | 9 |
| 61 | Evaporator Cover | 01072409 | 01072409 | 1 |
| 62 | Left Decorative Plate | 26112028 | 26112028 | 1 |
| 63 | Left Mounting Plate | 01332405 | 01332405 | 1 |
| 64 | Left Side Plate Foam | 12312401 | 12312401 | 1 |
| 65 | Bearing Mounting Plate | 01332406 | 01332406 | 1 |
| 66 | Rear Side Plate of Air outlet | 01302416 | 01302416 | 1 |
| 67 | Swing Connecting Rod | 10582008 | 10582008 | 2 |
| 68 | Swing Connecting Rod | 10582009 | 10582009 | 4 |
| 69 | Swing Fan | 10512027 | 10512027 | 26 |

Exploded View of Outdoor Unit

| Components and Parts List of Outdoor Unit |
| --- |
| No. | Description | Part Code | Qty |
|  |  | KFR-70W/dB1 |  |
| 1 | Signal Control Cable | 40032142 | 1 |
| 2 | Power Connecting Cable | 40020454 | 1 |
| 3 | Power Cable | 40032143 | 1 |
| 4 | Front Grill | 22265251 | 1 |
| 5 | Cabinet | 01435251 | 1 |
| 6 | Axial Flow Fan | 10335253 | 1 |
| 7 | Motor LW60L | 15013063 | 1 |
| 8 | Motor Support | 01705253 | 1 |
| 9 | Condenser Assy | 01103428 | 1 |
| 10 | Top Cover | 01255262 | 1 |
| 11 | Rear Grill | 01475252 | 1 |
| 12 | Underlay of Rear Grill | 76315252 | 1 |
| 13 | AC Contactor | 44010221 |  |
| 14 | Overload Protector | / | 1 |
| 15 | Capacitor CBB61 3.5μF/450V | 33010027 | 1 |
| 16 | Terminal Board 2-8 | 42011103 | 1 |
| 17 | Terminal Board T6C0A | 42011230 | 1 |
| 18 | Electric Box Assy | 01403707 | 2 |
| 19 | Wire Clamp# | 71010102 | 1 |
| 20 | Insulation Gasket C | 70410523 | 1 |
| 21 | Anti-phase Protector | / | 1 |
| 22 | Rear Side Plate Sub-assy | 0103709 | 2 |
| 23 | Left Handle | 26235401 | 1 |
| 24 | Valve Support Sub-assy | 1715002 | 1 |
| 25 | Gas Valve Sub-assy 5/8” | 07105251 | 1 |
| 26 | Valve 1/2” | 7100105 | 1 |
| 27 | Sensor Insert B | 42020063 | 1 |
| 28 | Compressor And Fittings | 0100065 |  |
| 29 | (Internal Inherent Protector) | Built in | 1 |
| 30 | Compressor Gasket | 76710209 | 1 |
| 31 | Isolation Sheet Sub-assy | 1235253 | 1 |
| 32 | Chassis Sub-assy | 1205263 | 1 |
| 33 | Handle | 26235252 | 1 |

Exploded View of Components and Parts of Outdoor Unit

| Components and Parts List of Outdoor Unit |
| --- |
| No. | Description | Part Code | Qty |
|  |  | KFR-70W/DNA1 | KF-70W/DNA1 |  |
| 1 | Signal Control Cable | 400321531 | 40032140 | 1 |
| 2 | Power Connecting Cable # | 40020454 | 40020454 | 1 |
| 3 | Power Cable # | 400203181 | 400203181 | 1 |
| 4 | Front Grill | 22265251 | 22265251 | 1 |
| 5 | Cabinet | 01435254 | 01435254 | 1 |
| 6 | Axial Flow Fan | 10335253 | 10335253 | 1 |
| 7 | Motor FW60L | 15013063 | 15013063 | 1 |
| 8 | Motor Support | 01705253 | 01705253 | 1 |
| 9 | Condenser Sub-assy | 011350302 | 01105039 | 1 |
| 10 | Top Cover | 01255262 | 01255262 | 1 |
| 11 | Rear Grill | 01475251 | 01475251 | 1 |
| 12 | Underlay of Rear Grill | 76315251 | 76315251 | 1 |
| 13 | Electric Box Assy | 01405001 | 01405001 |  |
| 14 | Capacitor CBB61 3μF/450V | 33010027 | 33010027 | 1 |
| 15 | Capacitor CBB65 40μF/450V | 33000022 | 33000022 | 1 |
| 16 | Bipolar AC Contactor | 44010221 | 44010221 | 1 |
| 17 | Terminal Board T480b | 42011231 | 42011231 | 1 |
| 18 | Terminal Board 2-8 | 42011103 | \ | 1 |
| 19 | Wire Clamp# | 71010102 | 71010102 | 1 |
| 20 | Insulation Gasket C | 70410523 | 70410523 | 1 |
| 21 | Gas-Liquid Separator Assy | 07255251 | 07255251 | 1 |
| 22 | Thermistor | 34030026 | \ | 1 |
| 23 | Sensor Insert B | 42020063 | \ | 1 |
| 24 | 4-way Valve (2 HP) | 430004031 | \ | 1 |
| 25 | 4-way Valve Fittings | 430004002 | \ | 1 |
| 26 | Rear Side Plate Sub-assy | 01303709 | 01303709 |  |
| 27 | Handle | 26235252 | 26235252 | 3 |
| 28 | Capillary Sub-assy | 03003431 | 03003432 | 1 |
| 29 | Valve Support Sub-assy | 01715001 | 01715001 | 1 |
| 30 | Outdoor Drainage Joint | 06123401 | \ | 1 |
| 31 | Liquid Valve Sub-assy | 07105002 | 07105002 | 1 |
| 32 | Gas Valve Sub-assy | 07105007 | 07105007 | 1 |
| 33 | Sound Absorbing Wool of Compressor | 75013118 | 75013118 | 1 |
| 34 | Compressor C-RN220H5B | 00100063 | 00100063 | 1 |
| 35 | (Internal Inherent Protector) | Built in | Built in | 1 |
| 36 | Compressor Gasket | 76710210 | 76710210 | 3 |
| 37 | Chassis Assy | 01203059 | 01203059 | 1 |
| 38 | Isolation Sheet Sub-assy | 01235253 | 01235253 | 1 |
| 39 | Front Side Plate | 01305247 | 01305247 | 1 |

Exploded View of Outdoor Unit

| Components and Parts List of Outdoor Unit |
| --- |
| No. | Description | Part Code | Qty |
|  |  | GST36-22L/A(0) |  |
| 1 | Signal Control Cable | 40032109 | 1 |
| 2 | Power Connecting Cable | 40020412 | 1 |
| 3 | Power Cable | 40020276 | 1 |
| 4 | Front Grill | 22265401 | 1 |
| 5 | Cabinet | 01435402 | 1 |
| 6 | Axial Flow Fan | 10335253 | 1 |
| 7 | Motor LW92A | 15015451 | 1 |
| 8 | Motor Support | 01705401 | 1 |
| 9 | Condenser Assy | 01103426 | 1 |
| 10 | Top Cover | 01255402 | 1 |
| 11 | Rear Grill | 01475401 | 1 |
| 12 | Underlay of Rear Grill | 76315251 | 1 |
| 13 | AC Contactor | 44010226 |  |
| 14 | Overload Protector | 46020112 | 1 |
| 15 | Capacitor CBB61 3.5μF/450V | 33010010 | 1 |
| 16 | Terminal Board 2-8 | 42011103 | 2 |
| 17 | Terminal Board GT8F0A1 | 42011036 | 1 |
| 18 | Electric Box Assy | 01403406 | 1 |
| 19 | Wire Clamp# | 71010102 | 2 |
| 20 | Insulation Gasket C | 70410523 | 1 |
| 21 | Anti-phase Protector | 46020052 | 1 |
| 22 | Rear Side Plate Sub-assy | 01305402 | 2 |
| 23 | Left Handle | 26235401 | 1 |
| 24 | Valve Support Sub-assy | 01715402 | 1 |
| 25 | Gas Valve Sub-assy 3/4” | 07103401 | 1 |
| 26 | Valve 1/2” | 07100105 | 1 |
| 27 | Sensor Insert E | 42020066 | 1 |
| 28 | Compressor And Fittings | 0010084 |  |
|  | (Internal Inherent Protector) | Built in |  |
| 29 | Compressor Gasket | 76710209 | 4 |
| 30 | Isolation Sheet Sub-assy | 01235403 | 1 |
| 31 | Chassis Sub-assy | 01205402 | 1 |
| 32 | Handle | 26235253 | 1 |
| 33 | Front Side Plate | 01305403 | 1 |

Exploded View of Outdoor Unit

| Components and Parts List of Outdoor Unit |
| --- |
| No. | Description | Part Code | Qty |
|  |  | GST36-22R/A(0) |  |
| 1 | Signal Control Cable# | 40032108 | 1 |
| 2 | Signal Control Cable# | 40032110 | 1 |
| 3 | Power Connecting Cable# | 40020412 | 1 |
| 4 | Power Connecting Cable# | 40020276 | 1 |
| 5 | Front Grill | 22265401 | 1 |
| 6 | Cabinet | 01435402 | 1 |
| 7 | Axial Flow Fan | 10335253 | 1 |
| 8 | Motor LW92A | 15015451 | 1 |
| 9 | Motor Support | 01705401 | 1 |
| 10 | Condenser Assy | 01103420 | 1 |
| 11 | Sensor Support | 24215101 | 1 |
| 12 | Top Cover | 01255402 | 1 |
| 13 | Rear Grill | 01475401 | 1 |
| 14 | Underlay of Rear Grill | 76315251 | 1 |
| 15 | AC Contactor | 44010226 | 1 |
| 16 | Overload Protector | 46020112 | 1 |
| 17 | Capacitor CBB61 3.5μF/450V | 33010010 | 1 |
| 18 | Terminal Board 2-8 | 42011103 | 2 |
| 19 | Anti-phase Protector | 46020052 | 1 |
| 20 | Terminal Board GT8F0A1 | 42011036 | 1 |
| 21 | Electric Box Assy | 01405401 | 2 |
| 22 | Wire Clamp# | 71010102 | 2 |
| 23 | Insulation Gasket C | 70410523 | 1 |
| 24 | Temp. Sensor | 39000199 | 1 |
| 25 | Sensor Insert B | 42020063 | 1 |
| 26 | 4-way Valve (5 HP) | 43000405 | 1 |
| 27 | 4-way Valve Fittings | 430004005 | 1 |
| 28 | Rear Side Plate Sub-assy | 01305402 | 1 |
| 29 | Left Handle | 26235401 | 1 |
| 30 | Auxiliary Capillary Sub-assy | 03003642 | 1 |
| 31 | Valve Support Sub-assy | 01715402 | 1 |
| 32 | Gas Valve Sub-assy 3/4” | 07103401 | 1 |
| 33 | Valve 1/2” | 07100105 | 1 |
| 34 | Outdoor Drainage Joint | 06123401 | 1 |
| 35 | Sensor Insert E | 42020066 | 1 |
|  | Compressor And Fittings | 00100184 | 1 |
| 36 | (Internal Inherent Protector) | Built in |  |
| 37 | Compressor Gasket | 76710209 | 4 |
| 38 | Isolation Sheet Sub-assy | 01235403 | 1 |
| 39 | Chassis Sub-assy | 01205402 | 1 |
| 40 | Handle | 26235253 | 1 |
| 41 | Front Side Plate | 01305403 | 1 |

Components and Parts List of Outdoor Unit

| Components and Parts List of Outdoor Unit |
| --- |
| No. | Description | Part Code | Qty |
|  |  | GST36-38R/A(0) |  |
| 1 | Signal Control Cable# | 400321531 | 1 |
| 2 | Power Connecting Cable# | 400204771 | 1 |
| 3 | Power Connecting Cable# | 40020454 | 1 |
| 4 | Front Grill | 22265401 | 1 |
| 5 | Cabinet | 01435402 | 1 |
| 6 | Axial Flow Fan | 10335253 | 1 |
| 7 | Motor LW92A | 15015451 | 1 |
| 8 | Motor Support | 01705401 | 1 |
| 9 | Condenser Assy | 01103426 | 1 |
| 10 | Top Cover | 01255402 | 1 |
| 11 | Rear Grill | 01475401 | 1 |
| 12 | Underlay of Rear Grill | 76315251 | 1 |
| 13 | AC Contactor | 44010226 | 1 |
| 14 | Overload Protector | 46020112 | 1 |
| 15 | Capacitor CBB61 3.5μF/450V | 33010020 | 1 |
| 16 | Terminal Board 2-8 | 42011103 | 2 |
| 17 | Terminal Board GT8F0A1 | 42011036 | 1 |
| 18 | Electric Box Assy | 01403406 | 1 |
| 19 | Wire Clamp# | 71010102 | 2 |
| 20 | Insulation Gasket C | 70410523 | 1 |
| 21 | Anti-phase Protector | 46020052 | 2 |
| 22 | Rear Side Plate Sub-assy | 01305402 | 2 |
| 23 | Left Handle | 26235401 | 1 |
| 24 | Valve Support Sub-assy | 01715402 | 1 |
| 25 | Gas Valve Sub-assy 3/4” | 7103401 | 1 |
| 26 | Valve 1/2” | 07100105 | 1 |
| 27 | Sensor Insert E | 42020066 | 1 |
| 28 | Compressor And Fittings | 00100185 | 1 |
|  | (Internal Inherent Protector) | Built in |  |
| 29 | Compressor Gasket | 76710209 | 4 |
| 30 | Isolation Sheet Sub-assy | 01235403 | 1 |
| 31 | Chassis Sub-assy | 01205402 | 1 |
| 32 | Handle | 26235253 | 1 |
| 33 | Front Side Plate | 01305403 | 1 |

Components and Parts List of Outdoor Unit

| Components and Parts List of Outdoor Unit |
| --- |
| No. | Description | Part Code | Qty |
|  |  | GST36-38R/A(0) |  |
| 1 | Signal Control Cable# | 40032142 | 1 |
| 2 | Signal Control Cable# | 40032143 | 1 |
| 3 | Power Connecting Cable# | 400204771 | 1 |
| 4 | Power Connecting Cable# | 40020454 | 1 |
| 5 | Front Grill | 22265401 | 1 |
| 6 | Cabinet | 01435402 | 1 |
| 7 | Axial Flow Fan | 10335253 | 1 |
| 8 | Motor LW92A | 15015451 | 1 |
| 9 | Motor Support | 01705401 | 1 |
| 10 | Condenser Assy | 01103420 | 1 |
| 11 | Sensor Support | 24215101 | 1 |
| 12 | Top Cover | 01255402 | 1 |
| 13 | Rear Grill | 01475401 | 1 |
| 14 | Underlay of Rear Grill | 76315251 | 1 |
| 15 | AC Contactor | 44010226 | 1 |
| 16 | Overload Protector | 46020112 | 1 |
| 17 | Capacitor CBB61 1.5μF/450V | 33010020 | 1 |
| 18 | Terminal Board 2-8 | 42011103 | 2 |
| 19 | Anti-phase Protector | 46020052 | 1 |
| 20 | Terminal Board GT8F0A1 | 42011036 | 1 |
| 21 | Electric Box Assy | 01405401 | 2 |
| 22 | Wire Clamp# | 71010102 | 2 |
| 23 | Insulation Gasket C | 70410523 | 1 |
| 24 | Temp. Sensor | 39000199 | 1 |
| 25 | Sensor Insert B | 42020063 | 1 |
| 26 | 4-way Valve (5 HP) | 43000405 | 1 |
| 27 | 4-way Valve Fittings | 430004002 | 1 |
| 28 | Rear Side Plate Sub-assy | 01305402 | 1 |
| 29 | Left Handle | 26235401 | 1 |
| 30 | Auxiliary Capillary Sub-assy | 03003437 | 1 |
| 31 | Valve Support Sub-assy | 01715402 | 1 |
| 32 | Gas Valve Sub-assy 3/4” | 07103401 | 1 |
| 33 | Valve 1/2” | 07100105 | 1 |
| 34 | Outdoor Drainage Joint | 06123401 | 1 |
| 35 | Sensor Insert E | 42020066 | 1 |
|  | Compressor And Fittings | 00100185 | 1 |
| 36 | (Internal Inherent Protector) | Built in |  |
| 37 | Compressor Gasket | 76710209 | 4 |
| 38 | Isolation Sheet Sub-assy | 01235403 | 1 |
| 39 | Chassis Sub-assy | 01205402 | 1 |
| 40 | Handle | 26235253 | 1 |
| 41 | Front Side Plate | 01305403 | 1 |

Components and Parts List of Outdoor Unit

| Components and Parts List of Outdoor Unit |
| --- |
| No. | Description | Part Code | Qty |
|  |  | GST36-100W/Db1-G |  |
| 1 | Signal Control Cable# | 40032142 | 1 |
| 2 | Signal Control Cable# | 40032143 | 1 |
| 3 | Power Connecting Cable# | 400204771 | 1 |
| 4 | Power Connecting Cable# | 40020454 | 1 |
| 5 | Front Grill | 22265401 | 1 |
| 6 | Cabinet | 01435402 | 1 |
| 7 | Axial Flow Fan | 10335401 | 1 |
| 8 | Motor | 15015401 | 1 |
| 9 | Motor Support | 01705401 | 1 |
| 10 | Condenser Assy | 01135402 | 1 |
| 11 | Room Temp. Sensor | 39000199 | 1 |
| 12 | Sensor Support | 24215101 | 1 |
| 13 | Top Cover | 01255402 | 1 |
| 14 | Rear Grill | 01475401 | 1 |
| 15 | AC Contactor | 44010226 | 1 |
| 16 | Overload Protector | 46020112 | 1 |
| 17 | Capacitor CBB61 3.5μF/450V | 33010010 | 1 |
| 18 | Terminal Board 2-8 | 42011103 | 2 |
| 19 | Anti-phase Protector | 46020052 | 1 |
| 20 | Terminal Board | 42011036 | 1 |
| 21 | Electric Box Assy | 01405401 | 2 |
| 22 | Wire Clamp# | 71010102 | 2 |
| 23 | Insulation Gasket C | 70410523 | 1 |
| 24 | Thermistor | 34030019 | 1 |
| 25 | Sensor Insert B | 42020063 | 1 |
| 26 | 4-way Valve | 43000405 | 1 |
| 27 | 4-way Valve Fittings | 430004002 | 1 |
| 28 | Rear Side Plate Sub-assy | 01305402 | 1 |
| 29 | Left Handle | 26235401 | 1 |
| 30 | Auxiliary Capillary Sub-assy | 03003659 | 1 |
| 31 | Valve Support Sub-assy | 01715402 | 1 |
| 32 | Gas Valve Sub-assy | 07103401 | 1 |
| 33 | Shutoff Valve Sub-assy | 071302331 | 1 |
|  | Joint End Cap | 06640104 | 1 |
|  | Union Nut | 06320006 | 1 |
| 34 | Outdoor Drainage Joint | 06123401 | 1 |
| 35 | Compressor | 00120043 | 1 |
| 36 | (Internal Inherent Protector) | Built in |  |
| 37 | Compressor Gasket | 76710209 | 4 |
| 38 | Thermistor | 34030026 | 1 |
| 39 | Sensor Insert E | 42020066 | 1 |
| 40 | Isolation Sheet Sub-assy | 01235403 | 1 |
| 41 | Chassis Sub-assy | 01205402 | 1 |
| 42 | Handle | 26235253 | 1 |
| 43 | Front Side Plate | 01305403 | 1 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | GST24-22R/A(0) | GST24-22L/A(0) |  |
| 1 | Signal Control Cable | 40032108 | / | 1 |
| 2 | Signal Control Cable | 40032110 | 40032109 | 1 |
| 3 | Power Connecting Cable # | 40020412 | 40020412 | 1 |
| 4 | Power Cable # | 400203031 | 400203031 | 1 |
| 5 | Front Grill | 22265251 | 22265251 | 1 |
| 6 | Cabinet | 01435254 | 01435254 | 1 |
| 7 | Axial Flow Fan | 10335253 | 10335253 | 1 |
| 8 | Motor FW60L | 15013063 | 15013063 | 1 |
| 9 | Motor Support | 01705253 | 01705253 | 1 |
| 10 | Condenser Sub-assy | 011350301 | 01135030 | 1 |
| 11 | Top Cover | 01255262 | 01255262 | 1 |
| 12 | Rear Grill | 01475251 | 01475251 | 1 |
| 13 | Underlay of Rear Grill | 76315251 | 76315251 | 1 |
| 14 | Electric Box Assy | 01403707 | 01403707 |  |
| 15 | Capacitor CBB61 3μF/450V | 33010010 | 33010010 | 1 |
| 16 | Capacitor CBB65 40μF/450V | 33000001 | 33000001 | 1 |
| 17 | Bipolar AC Contactor | 44010221 | 44010221 | 1 |
| 18 | Terminal Board T480b | 42011230 | 42011230 | 1 |
| 19 | Terminal Board 2-8 | 42011103 | / | 1 |
| 20 | Wire Clamp# | 71010102 | 71010102 | 2 |
| 21 | Insulation Gasket C | 70410523 | 70410523 | 1 |
| 22 | Gas-Liquid Separator Assy | 07255251 | 07255251 | 1 |
| 23 | Sensor Insert B | 42020063 | / | 3 |
| 24 | 4-way Valve (2 HP) | 43000403 | / | 1 |
| 25 | 4-way Valve Fittings | 430004005 | / | 1 |
| 26 | Rear Side Plate Sub-assy | 01305262 | 01305262 |  |
| 27 | Handle | 26235253 | 26235253 | 3 |
| 28 | Capillary Sub-assy | 03003443 | 03003442 | 1 |
| 29 | Valve Support Sub-assy | 01715001 | 01715001 | 1 |
| 30 | Outdoor Drainage Joint | 06123401 | / | 1 |
| 31 | Liquid Valve Sub-assy | 071037021 | 071037021 | 1 |
| 32 | Gas Valve Sub-assy | 071052521 | 071052521 | 1 |
| 33 | Damping Sound Absorbing Wool | 75015204 | 75015204 | 1 |
| 34 | Compressor ZR28K3-PFV-522 | 00100106 | 00100106 | 1 |
| 35 | (Internal Inherent Protector) | Built in | Built in | 1 |
| 36 | Chassis Sub-assy | 01205264 | 1205264 | 1 |
| 37 | Isolation Sheet Sub-assy | 01235253 | 1235253 | 1 |
| 38 | Front Side Plate | 01305247 | 1305247 | 1 |
| 39 | Thermistor GR20K1400CAP | 34030026 | 76710225 | 1 |
| 40 | Thermistor 100-052-00820 | 34030019 | / | 1 |
| 41 | Thermistor GR15K2350EPOXY | 34030030 | / | 1 |
| 42 | Compressor Foot Mat | 76710225 | 76710225 | 4 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | KFR-100W/DNA1-34005 | KF-100W/DNA1-34005 |  |
| 1 | Signal Control Cable # | 40032142 | \ | 1 |
| 2 | Signal Control Cable # | 40032143 | 400204771 | 1 |
| 3 | Power Connecting Cable # | 400204771 | 400204771 | 1 |
| 4 | Power Connecting Cable # | 40020454 | 40020454 | 1 |
| 5 | Front Grill | 22265401 | 22265401 | 1 |
| 6 | Cabinet | 01435402 | 01435402 | 1 |
| 7 | Axial Flow Fan | 10335401 | 10335401 | 1 |
| 8 | Motor FW92B | 15015401 | 15015401 | 1 |
| 9 | Motor Support | 01705401 | 01705401 | 1 |
| 10 | Condenser Sub-assy | 01103421 | 01103422 | 1 |
| 11 | Sensor Support | 24215101 | \ | 1 |
| 12 | Top Cover | 01255402 | 01255402 | 1 |
| 13 | Rear Grill | 01475401 | 01475401 | 1 |
| 14 | Underlay of Rear Grill | 76315251 | 76315251 | 1 |
| 15 | AC Contactor | 44010226 | 44010226 | 1 |
| 16 | Overload Protector | 46020112 | 46020112 | 1 |
| 17 | Capacitor CBB61 3.5μF/450V | 33010010 | 33010010 | 1 |
| 18 | Terminal Board 2-8 | 42011103 | 42011103 | 1 |
| 19 | Anti-phase Protector | 46020052 | 46020052 | 1 |
| 20 | Terminal Board GT8F0A1 | 42011036 | 42011036 | 2 |
| 21 | Electric Box Assy | 01405401 | 01405401 | 1 |
| 22 | Wire Clamp# | 71010102 | 71010102 | 1 |
| 23 | Insulation Gasket C | 70410523 | 70410523 | 3 |
| 24 | Temp. Sensor | 39000199 | \ | 1 |
| 25 | Sensor Insert B | 42020063 | \ | 1 |
| 26 | 4-way Valve (5 HP) | 430004051 | \ |  |
| 27 | 4-way Valve Fittings | 430004012 | \ | 3 |
| 28 | Rear Side Plate Sub-assy | 01305402 | 01305402 | 1 |
| 29 | Left Handle | 26235401 | 26235401 | 1 |
| 30 | Auxiliary Capillary Sub-assy | 03003492 | \ | 1 |
| 31 | Valve Support Sub-assy | 01715402 | 01715402 | 1 |
| 32 | Gas Valve Sub-assy | 07103406 | 07103406 | 1 |
| 33 | Liquid Valve Sub-assy | 07103405 | 07103405 | 1 |
| 34 | Outdoor Drainage Joint | 06123401 | \ | 1 |
| 35 | Sensor Insert E | 42020066 | 42020066 | 1 |
| 36 | Compressor And Fittings | 00100356 | 00100356 | 1 |
| 37 | (Internal Inherent Protector) | Built in | Built in | 1 |
| 38 | Compressor Gasket | 76710209 | 76710209 | 1 |
| 39 | Isolation Sheet Sub-assy | 01235403 | 01235403 | 1 |
| 40 | Chassis Sub-assy | 01205402 | 01205402 | 1 |
| 41 | Handle | 26235253 | 26235253 | 1 |
| 42 | Front Side Plate | 01305403 | 01305403 | 4 |

Components and Parts List of Outdoor Unit

| Components and Parts List of Outdoor Unit |
| --- |
| No. | Description | Part Code | Qty |
|  |  | KFR-120D/B1-G |  |
| 1 | Left Decorative Plate of Guide Plate Extruded Plastic Bar | 26112415 | 1 |
| 2 | Guide Louver I | 10512025 | 2 |
| 3 | Mounting Plate of Swing Louver | 01332409 | 1 |
| 4 | Guide Louver Holder | 24212019 | 4 |
| 5 | Guide Louver Support | 24212018 | 3 |
| 6 | Guide Louver | 10512026 | 3 |
| 7 | Guide Louver II | 10512408 | 1 |
| 8 | Right Decorative Plate of Guide Plate Extruded Plastic Bar | 26112416 | 1 |
| 9 | Mounting Plate (Left) of Swing Motor | 26152005 | 1 |
| 10 | Front Panel Sub-Assy | 01532413 | 1 |
| 11 | PCB Mounting Box | 20102138 | 1 |
| 12 | Display Board 6152J | 30546104 | 1 |
| 13 | Button Front Panel Sub-assy | 201620041 | 1 |
| 14 | Right Mounting Plate of Swing Motor | 26152006 | 1 |
| 15 | Stepping Motor (Air Guide) MP35CA | 15212402 | 1 |
| 16 | Swing Motor Clamp | 26112026 | 2 |
| 17 | Water Tray | 01272407 | 1 |
| 18 | Auxiliary Water Tray | 01272409 | 1 |
| 19 | Pipe Clip | 70812001 | 1 |
| 20 | Drainage Pipe Sub-assy | 05235433 | 1 |
| 21 | Handle | 26232001 | 4 |
| 22 | Right Side Plate Foam | 12312402 | 1 |
| 23 | Right Mounting Plate | 01332404 | 1 |
| 24 | Motor Bearing Block | 01792408 | 1 |
| 25 | Supporting Plate of Motor Support | 01792407 | 1 |
| 26 | Right Decorative Plate | 26112027 | 1 |
| 27 | Tube-exit Clamp of Evaporator | 01072425 | 1 |
| 28 | Electric Box Assy | 01403242 | 1 |
| 29 | Wire Seat | 24253001 | 1 |
| 30 | Wire-pressed Clamp | 24253002 | 1 |
| 31 | Terminal Board RS9413G | 42010178 | 1 |
| 32 | Fuse 5A 250VAC VDE | 46010013 | 1 |
| 33 | Mainboard 6152J | 30036052 | 1 |
| 34 | Ring of Bearing | 76512404 | 2 |
| 35 | Fan Bearing | 76512210 | 2 |
| 36 | Power Transformer SC28D | 43110194 | 1 |
| 37 | Electric Box Cover | 01413008 | 1 |
| 38 | Centrifugal Fan | 10319051 | 4 |
| 39 | Shaft Assy | 73012402 | 2 |
| 40 | Capacitor CBB61 | 33010012 | 1 |

| 41 | Capacitor Support | 01722405 | 1 |
| --- | --- | --- | --- |
| 42 | Motor FN150A | 15012405 | 1 |
| 43 | Motor Fixing Clip | 01722410 | 1 |
| 44 | Motor Clamp | 01702405 | 1 |
| 45 | Shaft Coupling | 73012403 | 2 |
| 46 | Mounting Board Sub-assy of Motor | 01332425 | 1 |
| 47 | Front Propeller Housing | 22202030 | 4 |
| 48 | Rear Propeller Housing | 22202029 | 4 |
| 49 | Rear Side Plate Assy | 01302411 | 1 |
| 50 | Motor Support Sub-assy | 01702411 | 1 |
| 51 | Filter | 11122013 | 1 |
| 52 | Gate Sub-assy | 01362407 | 1 |
| 53 | Front Grill | 22412010 | 4 |
| 54 | Front Grill Clasp 2 | 26252003 | 8 |
| 55 | Remote Controller Y512 （GREE） | 30512506 | 1 |
| 56 | Evaporator Assy | 01002401 | 1 |
| 57 | Front Grill Clasp 1 | 26252002 | 8 |
| 58 | Temp. Sensor (20K) | 390001215 | 1 |
| 59 | Sensor Insert B | 42020063 | 1 |
| 60 | Capillary | 81020196 | 9 |
| 61 | Evaporator Cover | 01072409 | 1 |
| 62 | Left Decorative Plate | 26112028 | 1 |
| 63 | Left Mounting Plate | 01332405 | 1 |
| 64 | Left Side Plate Foam | 12312401 | 1 |
| 65 | Bearing Mounting Plate | 01332406 | 1 |
| 66 | Rear Side Plate of Air outlet | 01302416 | 1 |
| 67 | Swing Connecting Rod | 10582008 | 2 |
| 68 | Swing Connecting Rod | 10582009 | 4 |
| 69 | Swing Fan | 10512027 | 26 |

Components and Parts List of Outdoor Unit

| Components and Parts List of Outdoor Unit |
| --- |
| No. | Description | Part Code | Qty |
|  |  | KFR-100W/DNA1-34005 | KF-100W/DNA1-34005 |  |
| 1 | Signal Control Cable # | 40032142 | \ | 1 |
| 2 | Signal Control Cable # | 40032143 | 400321531 | 1 |
| 3 | Power Connecting Cable # | 400204771 | 400204772 | 1 |
| 4 | Power Connecting Cable # | 40020454 | 400204771 | 1 |
| 5 | Front Grill | 22265251 | 22265251 | 2 |
| 6 | Cabinet | 01435433 | 01435433 | 1 |
| 7 | Axial Flow Fan | 10335253 | 10335253 | 2 |
| 8 | Motor FW68T | 15013302 | 15013302 | 2 |
| 9 | Motor Support Sub-assy | 01705433 | 01705433 | 1 |
| 10 | Condenser Sub-assy | 01133455 | 011054381 | 1 |
| 11 | Thermistor | 34030030 | \ | 1 |
| 12 | Sensor Support | 24215101 | \ | 1 |
| 13 | Top Cover | 01255262 | 01255262 | 1 |
| 14 | Underlay of Rear Grill | 76315251 | 76315251 | 1 |
| 15 | Rear Grill | 01475431 | 01475431 | 1 |
| 16 | Thermistor | 34030031 | \ | 1 |
| 17 | Sensor Insert B | 42020063 | \ | 1 |
| 18 | Electric Box Assy | 01405471 | 01405471 | 1 |
| 19 | AC Contactor | 44010226 | 44010226 | 1 |
| 20 | Anti-phase Protector | 46020052 | 46020052 | 1 |
| 21 | Overload Protector | 46020103 | 46020103 | 1 |
| 22 | Terminal Board T8F0A | 42011224 | 42011036 | 1 |
| 23 | Capacitor CBB61 3.5μF/450V | 33010010 | 33010010 | 1 |
| 24 | Terminal Board 2-8 | 42011103 | 42011103 | 1 |
| 25 | Wire Clamp# | 71010102 | 71010102 | 2 |
| 26 | Insulation Gasket C | 70410523 | 70410523 | 1 |
| 27 | Capillary Sub-assy | 030037131 | 30037141 | 1 |
| 28 | 4-way Valve (5 HP) | 430004051 | \ | 1 |
| 29 | 4-way Valve Fittings | 430004005 | \ | 1 |
| 30 | Gas-Liquid Separator Assy | 07225433 | 07225433 | 1 |
| 31 | Thermistor | 34030019 | 34030019 | 1 |
| 32 | Sensor Insert E | 42020066 | 42020066 | 1 |
| 33 | Rear Side Plate Sub-assy | 01303712 | 01303712 | 1 |
| 34 | Handle | 26235253 | 26235253 | 2 |
| 35 | Valve Support Sub-assy | 01715001 | 01715001 | 1 |
| 36 | Liquid Valve Sub-assy | 07103704 | 07103704 | 1 |
| 37 | Gas Valve Sub-assy | 07103703 | 07103703 | 1 |
| 38 | Outdoor Drainage Joint | 06123401 | 06123401 | 1 |
| 39 | Compressor C-SBN353H8A | 00100157 | 00100157 | 1 |
| 40 | (Internal Inherent Protector) | Built in | Built in |  |
| 41 | Compressor Gasket | 76710209 | 76710209 | 4 |
| 42 | Chassis Sub-assy | 01205433 | 01205433 | 1 |
| 43 | Chassis Assy | 01235440 | 01235440 | 1 |
| 44 | Front Side Plate | 01305431 | 01305431 | 1 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | GST42-22R/A(0) | GST42-22L/A(0) |  |
| 1 | Signal Control Cable | 40032110 | 40032109 | 1 |
| 2 | Power Connecting Cable | 40020412 | 40020412 | 1 |
| 3 | Power Cable | 40020276 | 40020276 | 1 |
| 4 | Front Grill | 22265251 | 22265251 | 2 |
| 5 | Rear Grill | 01475431 | 01475431 | 1 |
| 6 | Cabinet | 01435433 | 01435433 | 1 |
| 7 | Top Cover | 01255262 | 01255262 | 1 |
| 8 | Underlay of Rear Grill | 76315251 | 76315251 | 1 |
| 9 | Condenser Assy | 011054442 | 011034512 | 1 |
| 10 | Motor Support Sub-assy | 01705433 | 01705433 | 1 |
| 11 | Motor FW68E | 15013712 | 15013712 | 2 |
| 12 | Isolation Sheet | 01235441 | 01235441 | 1 |
| 13 | Gas-Liquid Separator Assy | 07225433 | 07225433 | 1 |
| 14 | 4-way Valve Fittings | 430004005 | / | 1 |
| 15 | 4-way Valve | 43000405 | / | 1 |
| 16 | Sensor Insert B | 42020066 | 42020066 | 1 |
| 17 | Capillary Assy | 030034101 | 030034341 | 1 |
| 18 | Valve 1/2” | 07100105 | 07100105 | 1 |
| 19 | Gas Valve Sub-assy | 07103401 | 07103401 | 1 |
| 20 | Compressor And Fittings | 00100035 | 00100035 | 1 |
|  | Internal (Inherent Protector) | Built in | Built in | 1 |
| 21 | Compressor Gasket | 76710209 | 76710209 | 4 |
| 22 | Axial Flow Fan | 10335253 | 10335253 | 2 |
| 23 | Electric Box Assy | 01405471 | 01405471 | 1 |
| 24 | Terminal Board 2-8 | 42011103 | 42011103 | 1 |
| 25 | Capacitor CBB61 3μF/450V | 33010027 | 33010027 | 2 |
| 26 | Overload Protector | 46020114 | 46020114 | 1 |
| 27 | Terminal Board T8F0B | 42011239 | 42010177 | 1 |
| 28 | Wire Clamp | 71010102 | 71010102 | 2 |
| 29 | Insulation Gasket C | 70410523 | 70410523 | 2 |
| 30 | Anti-phase Protector | 46020066 | 46020066 | 1 |
| 31 | AC Contactor | 44010214 | 44010214 | 1 |
| 32 | Handle | 26235253 | 26235253 | 3 |
| 33 | Valve Support Sub-assy | 01715001 | 01715001 | 1 |
| 34 | Rear Side Plate | 01305434 | 01305434 | 1 |
| 35 | Front Side Plate | 01305431 | 01305431 | 1 |
| 36 | Chassis Sub-assy | 01205433 | 01205433 | 1 |
| 37 | Bellows Sub-assy ф19 | 050100613 | 050100611 | 1 |
| 38 | Bellows ф19 | 05010059 | 04010058 | 1 |
| 39 | Bellows ф12 | 05010058 | 05010059 | 1 |
| 40 | Bellows Sub-assy ф12 | 050100611 | / | 1 |
| 41 | Signal Control Cable | 40032108 | / | 1 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | GST42-38R/A(0) | GST42-38L/A(0) |  |
| 1 | Signal Control Cable | 40032110 | 40032109 | 1 |
| 2 | Power Connecting Cable | 40020412 | 40020412 | 1 |
| 3 | Power Cable | 40020297 | 40020297 | 1 |
| 4 | Front Grill | 22265251 | 22265251 | 2 |
| 5 | Rear Grill | 01475431 | 01475431 | 1 |
| 6 | Cabinet | 01435433 | 01435433 | 1 |
| 7 | Top Cover | 01255262 | 01255262 | 1 |
| 8 | Underlay of Rear Grill | 76315251 | 76315251 | 1 |
| 9 | Condenser Assy | 011054441 | 011034511 | 1 |
| 10 | Motor Support Sub-assy | 01705433 | 01705433 | 1 |
| 11 | Motor FW68E | 15013712 | 15013712 | 2 |
| 12 | Isolation Sheet | 01235441 | 01235441 | 1 |
| 13 | Gas-Liquid Separator Assy | 07225433 | 07225433 | 1 |
| 14 | 4-way Valve Fittings | 430004005 | / | 1 |
| 15 | 4-way Valve | 43000405 | / | 1 |
| 16 | Sensor Insert B | 42020066 | 42020066 | 1 |
| 17 | Capillary Assy | 03003410 | 03003434 | 1 |
| 18 | Valve 1/2” | 07100105 | 07100105 | 1 |
| 19 | Gas Valve Sub-assy | 07103401 | 07103401 | 1 |
| 20 | Compressor And Fittings | 00120044 | 00120044 | 1 |
|  | Internal (Inherent Protector) | Built in | Built in | 1 |
| 21 | Compressor Gasket | 76710209 | 76710209 | 4 |
| 22 | Axial Flow Fan | 10335253 | 10335253 | 2 |
| 23 | Electric Box Assy | 01405471 | 01405471 | 1 |
| 24 | Terminal Board 2-8 | 42011103 | 42011103 | 1 |
| 25 | Capacitor CBB61 3μF/450V | 33010027 | 33010027 | 2 |
| 26 | Overload Protector | 46020112 | 46020103 | 1 |
| 27 | Terminal Board T8F0B | 42011224 | 42011036 | 1 |
| 28 | Wire Clamp | 71010102 | 71010102 | 2 |
| 29 | Insulation Gasket C | 70410523 | 70410523 | 2 |
| 30 | Anti-phase Protector | 46020052 | 46020052 | 1 |
| 31 | AC Contactor | 44010226 | 44010226 | 1 |
| 32 | Handle | 26235252 | 26235252 | 3 |
| 33 | Valve Support Sub-assy | 01715001 | 01715001 | 1 |
| 34 | Rear Side Plate | 01305434 | 01305434 | 1 |
| 35 | Front Side Plate | 01305431 | 01305431 | 1 |
| 36 | Chassis Sub-assy | 01205433 | 01205433 | 1 |
| 37 | Bellows Sub-assy ф19 | 050100613 | 050100611 | 1 |
| 38 | Bellows ф19 | 05010059 | 04010059 | 1 |
| 39 | Bellows ф12 | 05010058 | 05010058 | 1 |
| 40 | Bellows Sub-assy ф12 | 050100611 | / | 1 |
| 41 | Signal Control Cable | 40032108 | / | 1 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | GST60-22R/A(0) | GST60-22L/A(0) |  |
| 1 | Signal Control Cable | 40032110 | 40032109 | 1 |
| 2 | Power Connecting Cable | 40020412 | 40020412 | 1 |
| 3 | Power Cable | 400203081 | 400203081 | 1 |
| 4 | Front Grill | 22265251 | 22265251 | 2 |
| 5 | Rear Grill | 01475431 | 01475431 | 1 |
| 6 | Cabinet | 01435433 | 01435433 | 1 |
| 7 | Top Cover | 01255262 | 01255262 | 1 |
| 8 | Underlay of Rear Grill | 76315251 | 76315251 | 1 |
| 9 | Condenser Assy | 01103439 | 01103425 | 1 |
| 10 | Motor Support Sub-assy | 01708732 | 01708732 | 1 |
| 11 | Motor LW92A | 15015451 | 15015451 | 2 |
| 12 | Isolation Sheet | 01235172 | 01235172 | 1 |
| 13 | Gas-Liquid Separator Assy | 07225479 | 07225479 | 1 |
| 14 | 4-way Valve Fittings | 430004005 | / | 1 |
| 15 | 4-way Valve | 43000405 | / | 1 |
| 16 | Sensor Insert B | 42020066 | 42020066 | 1 |
| 17 | Capillary Assy | 3003446 | 3003444 | 1 |
| 18 | Valve 1/2” | 07100105 | 07100105 | 1 |
| 19 | Gas Valve Sub-assy | 07103401 | 07103401 | 1 |
| 20 | Compressor And Fittings | 00100329 | 00100329 | 1 |
|  | Internal (Inherent Protector) | Built in | Built in | 1 |
| 21 | Compressor Gasket | 76710209 | 76710209 | 4 |
| 22 | Axial Flow Fan | 10335253 | 10335253 | 2 |
| 23 | Electric Box Assy | 01405471 | 01405471 | 1 |
| 24 | Terminal Board 3-12 | 42011251 | 42011251 | 1 |
| 25 | Capacitor CBB61 1.5μF/450V | 33010020 | 33010020 | 2 |
| 26 | Overload Protector | 46020120 | 46020120 | 1 |
| 27 | Terminal Board T8F0B | 42011239 | 42010177 | 1 |
| 28 | Wire Clamp | 71010102 | 71010102 | 2 |
| 29 | Insulation Gasket C | 70410523 | 70410523 | 2 |
| 30 | Anti-phase Protector | 46020066 | 46020066 | 1 |
| 31 | AC Contactor | 44010214 | 44010214 | 1 |
| 32 | Handle | 26235253 | 26235253 | 3 |
| 33 | Valve Support Sub-assy | 01715001 | 01715001 | 1 |
| 34 | Rear Side Plate | 01305434 | 01305434 | 1 |
| 35 | Front Side Plate | 01305431 | 01305431 | 1 |
| 36 | Chassis Sub-assy | 01205472 | 01205472 | 1 |
| 37 | Bellows Sub-assy ф19 | 050100613 | 050100611 | 1 |
| 38 | Bellows ф19 | 05010059 | 04010059 | 1 |
| 39 | Bellows ф12 | 05010058 | 05010058 | 1 |
| 40 | Bellows Sub-assy ф12 | 050100611 | / | 1 |
| 41 | Signal Control Cable | 40032108 | / | 1 |

| No. | Description | Part Code | Qty |
| --- | --- | --- | --- |
|  |  | GST60-38R/A(0) | GST60-38L/A(0) |  |
| 1 | Signal Control Cable | 40032110 | 40032110 | 1 |
| 2 | Power Connecting Cable | 40020412 | 40020412 | 1 |
| 3 | Power Cable | 400203091 | 400203091 | 1 |
| 4 | Front Grill | 22265251 | 22265251 | 2 |
| 5 | Rear Grill | 01475431 | 01475431 | 1 |
| 6 | Cabinet | 01435433 | 01435433 | 1 |
| 7 | Top Cover | 01255262 | 01255262 | 1 |
| 8 | Underlay of Rear Grill | 76315251 | 76315251 | 1 |
| 9 | Condenser Assy | 01103439 | 01103425 | 1 |
| 10 | Motor Support Sub-assy | 01708732 | 01708732 | 1 |
| 11 | Motor LW92A | 15015451 | 15015451 | 2 |
| 12 | Isolation Sheet | 01235472 | 01235472 | 1 |
| 13 | Gas-Liquid Separator Assy | 07225479 | 07225479 | 1 |
| 14 | 4-way Valve Fittings | 430004005 | / | 1 |
| 15 | 4-way Valve | 43000405 | / | 1 |
| 16 | Sensor Insert B | 42020066 | 42020066 | 1 |
| 17 | Capillary Assy | 03003446 | 03003444 | 1 |
| 18 | Valve 1/2” | 07100105 | 07100105 | 1 |
| 19 | Gas Valve Sub-assy | 07103401 | 07103401 | 1 |
| 20 | Compressor And Fittings | 00100159 | 00100159 | 1 |
| 21 | Internal (Inherent Protector) | Built in | Built in | 4 |
| 22 | Compressor Gasket | 76710209 | 76710209 | 2 |
| 23 | Axial Flow Fan | 10335253 | 10335253 | 1 |
| 24 | Electric Box Assy | 01405471 | 01405471 | 2 |
| 25 | Terminal Board 3-12 | 42011251 | 42011251 | 2 |
| 26 | Capacitor CBB61 1.5μF/450V | 33010020 | 33010020 | 2 |
| 27 | Overload Protector | 46020114 | 46020114 | 1 |
| 28 | Terminal Board T8F0B | 42011224 | 42011224 | 1 |
| 29 | Wire Clamp | 71010102 | 71010102 | 2 |
| 30 | Insulation Gasket C | 70410523 | 70410523 | 2 |
| 31 | Anti-phase Protector | 46020052 | 46020052 | 1 |
| 32 | AC Contactor | 44010214 | 44010214 | 3 |
| 33 | Handle | 26235253 | 26235253 | 1 |
| 34 | Valve Support Sub-assy | 01715001 | 01715001 | 1 |
| 35 | Rear Side Plate | 01305434 | 01305434 | 1 |
| 36 | Front Side Plate | 01305431 | 01305431 | 1 |
| 37 | Chassis Sub-assy | 01205472 | 01205472 | 1 |
| 38 | Bellows Sub-assy ф19 | 050100613 | 050100613 | 1 |
| 39 | Bellows ф19 | 05010059 | 04010059 | 1 |
| 40 | Bellows ф12 | 05010058 | 05010058 | 1 |
| 41 | Bellows Sub-assy ф12 | 050100611 | / | 1 |
| 42 | Signal Control Cable | 40032108 | / | 1 |

Care and Maintenance

Warning

- Be sure to stop the unit and plug off the power before cleaning your air conditioner. Otherwise, electric shock may happen.

- Wetting of air conditioner may cause the risk of electric shock. Make sure not to wash your air conditioner in any case.

- Volatile liquids such as thinner or gasoline will cause damage to the appearance of air conditioner. (Only use soft dry cloth or wet cloth soaked with neutral detergent to clean the air conditioner cabinet).

To clean the filter

Remove the filter and rinse it with vacuum cleaner or water. If very dirty, wash with warm water (below 45℃) that is added with neutral detergent. Fully dry the filter before reinstallation.

Suggestion: Too dirty filter will reduce air inflow and result in system overload, causing 6% more consumption of power. Therefore, it is quite necessary to clean the filter regularly.

To clean the equipment and components

Use dry and soft cloth or vacuum cleaner to clean the air conditioner and remote controller. If wet cloth is used, please wipe it dry after cleaning.

Warning: Never expose the front grill or air filter directly under the sun. Never clean it with hot water over 45℃ or dry it on fire, (as this will cause decoloring, fire or deformation).

When using the air conditioner

Check for any foreign articles that may obstruct the air into or out of the indoor and outdoor unit.

If the unit is operating without air filter, dust will deposit and cause trouble to the unit. Generally, be sure to install filter before operating the unit.

Check the drainage pipe for bend or damage.

Check the equipment for normal and correct installation.

When the air conditioner is out of service

Pull off the plug and disconnect the power.

Clean the filer, equipment and components.

Start the fan for 2 to 3 hours to clean and dry the inside of the equipment.

Trouble-Shooting

In case of the following protection or failures, the indoor unit shall display corresponding codes, which are explained as follows: Code Explanation E1 Compressor High-pressure Protection E2 Indoor Antifreeze Protection E3 Compressor Low-pressure Protection E4 Exhaust Pipe High-temp. Protection E5 Low-voltage Protection

# Text boxes

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Block or breakage of drainage pipe

Replace drainage pipe

The refrigerant pipe joint is not wrapped firmly

Wrap and bind it again firmly

Abnormal electromagnetic noise from 4-way valve when in heating operation

Internal short circuit of solenoid valve, replace solenoid valve

Abnormal sound from inside compressor

Replace Compressor

Indoor fan bumps cabinet

Adjust fan position

- Tighten connection screws

- Attach vibration damping gum between metal plates

Metal plates bump together inside the unit

Abnormal sound and vibration

Pipes of outdoor unit bump together

Separate bumping pipes

Adjust support foot mat of compressor, tighten loose bolts

Vibration of compressor is violent

Foreign articles inside the indoor unit

Remove foreign articles

Seat-and-Ceiling Mounted Series

Fan of indoor unit touches other positions

Adjust fan position

Controller is damaged (IC2003 is damaged, swing relay cannot close

Swing louver does not run

Wrong line connection

Torque of swing motor is insufficient

Fisrtly check if line connections have fault, if no, replace components at failure position

Replace protector

Failure of protector itself

Replace Compressor

Compressor does not operate smoothly (seized or jammed), air discharge valve is damaged

Compressor is overheated so protector is activated

Replace capillary

Capillary is blocked so air intake temperature is too high

Adjust refrigerant amount

Insufficient or too much refrigerant

Failure of protector itself

Use uniersal meter to check if contacts of compressure not overheated are conducting; replace protector in case of non-conducting conditions

Wrong line connection

It is suggested to equip voltage regulator

Voltage is too low or too high

Operating capacitor of compressor is damaged

Compressor failure

Correctly connect lines according to electrical diagram

Replace capcitor

When in cooling or heating mode, outdoor fan operates but compressor does not operate

Replace Compressor

Replace fan capacitor

Outdoor fan capacitor is damaged

Wrong line connection

Correctly connect lines according to electrical diagram

When in cooling or heating mode, compressor operates but outdoor fan does not operate

Outdoor fan motor is damaged

Replace fan motor

Replace it withfan capacitor of the same model and spec

Open circuit or damage of fan capacitor

Correctly connect lines according to electrical diagram

Wrong line connection

When air supply mode is selected, the fan does not operate

The internal overheating protector frequently breaks as overheating is caused by abnormity of motor

Replace fan motor

Replace fan motor or components with failure

Indoor fan motor burned out or there is wire breakage or failure of overheating protector

Seat-and-Ceiling Mounted Series

Seat-and-Ceiling Mounted Series

Keep the indoor space as closed as possible, do not use electrical appliance generating large amount of heat

Indoor space is not sufficiently closed, or people enters or leave the room frequently, or there is heating equipment operating in the room

Install proper weather screen; it is suggested to replace air-conditioner unit with one of higher capacity in case the best available cooling effect does not satisfy needs

Outdoor temperature is too high

Outdoor unit shall be installed in a place with good ventilation

Mounting position of outdoor unit is inappropriate

Replace motor

Motor is damaged

Replace capcitor

Capacitor

is damaged

Fan speed turns lower

Set fan speed as high or medium

Fan speed was set too low

Clean filter

Block in air filter

Wash away dust on surface

of heat exchanger

Block in outdoor heat exchanger

Insufficient air circulation volume

The thermal insulation of big pipe and small pipe shall be separate and sound; joint and bare position of copper pipe shall also have thermal insulation

Poor thermal insulation of connecting pipe between indoor unit and outdoor unit

Observe the condensation condition of evaporator or the reading of high pressure meter to judge if the system is blocked; deal with the system accordingly

Block in cooling system

Replace capillary

Partial block in capillary

Replace 4-way valve

4-way valve failure

Replace compressor

Leakage between internal high pressure and low pressure sections of compressor

Check leakage, carry out vacuum-pumping after repairing leakage and charge refrigerant according to requirements

Leakage of refrigerant or insufficient refrigerant

Failure of refrigerant flow

Check the forecasted cooling (heating) load

Check if the cooling (heating) load is appropriate

Adjust the set temperature

Set temperature is not appropriate

Poor cooling (heating) effect

Power voltage is too low

Failure of air-conditioning unit or component insulation failure, short circuit or electricle leakage owing to insulation puncture after heating, measure insulation resistance or check the components one by one to find the ones with failure; failure of circuit breaker itself, replace it.

When turning the air-conditioning unit to the “ON”status, trip of circuit breaker occurs several minutes later

Check power voltage. If the voltage is 10% than rated voltage, check the cause, and improve the power supply conditions such as adding regulated power supply.

First press “AUTO” key of manual switch. If there is no action check according to the above method; if the operation is normal after pressing the key, recheck to see if the mounting position of receiving head and the line connections are correct; if they are correct, replace receiving head or remote controller.

Replace battery

Receiving head is damaged

Receiving head is loose or plug connection is poor

Remote

controller failure

Batteries of remote controller are running out of power

Controller is damaged

Replace controller

Connection line of transformer is loose or suffers from poor plugging, or there is transformer failure

Secure line connections; measure output voltage of transformer and replace transformer if it is incorrect

Controller fuse burned out

Replace controller fuse

Power plug is not firmly seated or connection is poor

Check and secure the plug to ensure firm contact

No power supply

Check power supply line

Remote controller does not receive signal (when unit is powered on, buzzer shall sound, unless buzzer is damaged)

When air-conditioning unit is powered on, there is no action (when the unit is plugged in, buzzer does not sound and there is no action after using the remote controller to start the unit)

When set short-circuiter as “ON”, it trips immediately

Check insulation resistance for grounding; Confirm if air-conditioning unit has electrical leakage or is short-circuited

Trip of circuit breaker or burn-out of fuse

Air –conditioning unit

cannot be started

Water leakage

Seat-and-Ceiling Mounted Series

Tpreset

Tpreset

Tpreset

Tpreset

Tpreset

Tpreset

Tpreset

Tpreset

Tpreset

Tpreset

Tpreset

Tpreset

SWING key

One press of this key will enable the guide louver to swing at a specific angle. Another press will stop the guide louver.

TEMP. key

Each press of (+) key will increase the preset temperature by 1℃. Each press of (-) key will decrease the preset temperature by 1℃.

Under “ “ mode, the indoor temperature can be adjusted to any value between 16~30℃.

MODE key

The run mode will change sequentially as below with each press of MODE key.

Auto

FAN key

Each press of this key will change the fan speed sequentially as below:

Auto Fan

Note: The fan speed is not adjustable under  Mode.

Cooling mode

Dehumidifying mode

Fan mode

Heating Mode

ON/OFF key

Press this key to start the air conditioner. Press it again to stop the air conditioner.

LCD display

Display the information selected by each key

SLEEP key

Press this key to enter into sleep mode and press it again to exit sleep mode.

Note: There is no sleep function under Auto or Fan mode.

AUTO OFF key

Pressing this key when the unit is running, you can set the AUTO OFF time from 0 to 24 hours.

Cancel the AUTO ON/OFF

Lamp indicator

Press this key to switch on the lamp. Press it again to switch off the lamp.

AUTO ON key

Pressing this key when the unit is stopped, you can set the AUTO ON time from 0 to 24 hours. Each press of this key will increase the time by 0.5 hour.

Cancel the

AUTO ON/OFF

Battery cover

Screw

(Fig 8-3)

Installing dimension

Overall dimension